## კრებსითი
სასტერილიზაციო ბლოკის საინჟინრო სისტემების მოწყობის ღირებულება
გათბობა-კონდიცირება-ვენტილაცია, სუფთა ზონების სტანდარტით
ძალოვანი ელექტრობა
სულ
ტარნსპორტი | 2%
ჯამი
ზედნადები ხარჯი | 7%
ჯამი
მოგება | 10%
ჯამი
დღგ | 18%
სულ, ჯამი

## HVAC
BOQ - Ventilation of Sterilization Block of Iashvili clinic (Freon cooling)
Units, materials | Meas | Q-ty | Unit price | Sum | Labor, unit | Sum | Subtotal
Package Air handling unit L=6000m3/h dP=900Pa, Qc=32kW, Qh=42kW, Mixing Box, PreFilter F5, Filter F9, Nel=5,5kW, silencer, full automatic (3-way valves with actuators, frequency invertor, control panel, air intake damper with actuator, filter differential pressure gauges), outdoor condenser. | Compl | 1
Copper piping between unit and condenser | Compl | 1
Drainage pump, G=0,5m3/h, H=6m | pc | 1
Exhaust fan L=700m3/h, dP=200Pa, with variable speed driver (VFD 0,35kW) and silencer, air damper with actuator | Compl | 1
HEPA filter H14, 570x570x117mm with plenum 625X625mm and swirl diffuser | Compl | 11
HEPA filter H14, 305x305x117mm with plenum 415X415mm and swirl diffuser | Compl | 1
Galvanized sheet steel air duct µ=0,55mm | m2 | 121
Armaflex insulation Δ=10mm | m2 | 65
Hangers and Fixture for air ducts | Compl | 1
Flexible duct D200mm with insulation | m | 50
Air volume damper 600x250mm | pc | 1
Air volume damper 500x250mm | pc | 1
Air volume damper 400x200mm | pc | 1
Air volume damper 250x200mm | pc | 1
Gravity damper 600x300mm | pc | 1
One row Exhaust grille 400x200mm with damper | pcs | 6
One row Exhaust grille 400x150mm with damper | pcs | 4
One row Exhaust grille 300x100mm with damper | pcs | 4
Recirculation unit with HEPA filtration | Compl | 1
Inverter Split AC unit, 24 000BTU | compl | 1
AC unit piping (copper pipe) | compl | 1
Connection to existing heating system | Compl | 1
Drainage piping | Compl | 1
Additional installation materials | Compl | 1
System Adjusting and Start Up | Compl | 1
SUM

## Electricity
BOQ - Electricity of Sterilization Block of Iashvili clinic
Units, materials | Meas | Q-ty | Unit price | Sum | Labor, unit | Sum | Sub total
Power Cable
Power Cable NHXMH-J 3X1.5 | m | 100
Power Cable NHXMH-J 3X2.5 | m | 100
Power Cable NHXMH-J 3X4 | m | 80
Power Cable NHXMH-J 5X1.5 | m | 20
Power Cable N2XH-J 5X6 | m | 50
Power Cable N2XH-J 5X10 | m | 30
PDB
MCCB 3P 200A 36kA +SHT 220Vac | pcs. | 1
MCB 3P C63A 6kA | pcs. | 2
MCB 3P C40A 6kA | pcs. | 1
MCB 3P C10A 6kA | pcs. | 1
MCB 1P C25A 6kA | pcs. | 2
MCB 1P C20A 6kA | pcs. | 1
MCB 1P C16A 6kA | pcs. | 2
MCB 1P C10A 6kA | pcs. | 4
Distribution Block 1 pole, 250A | pcs. | 4
Distribution Block 1 pole, 125A | pcs. | 1
Insulated busbar 80A, L1,L2,L3 | Te. | 10
voltage relay | pcs. | 1
switchboard H800XW500XD210 | set | 1
installation materials | set | 1
Supporting material
cable tray W100/H11/L2000 | m | 42
cable tray W200/H11/L2000 | m | 3
cable tray wall mount 100 | pcs. | 42
cable tray wall mount 200 | pcs. | 2
cable tray joint | pcs. | 30
installation materials | set | 1
SUM, USD