Annex N2

Technical Assignment

- Purchase of power cells for # 8 and # 9 850 kW engines in 6 KW distributor injection pump of “Bagebi” Pumping Station

Size (cm)

  - Height: 200 (± 5)

  - Width: 90 (± 5)

  - Depth: 100 (± 5)

- The distribution box should be equipped with the following devices:

  - switch: 6-10 kV voltage, 400 amps, with stationary grounding

  - Line switch: 6-10 kV voltage, 400 amps, with stationary grounding

  - Power transformer: ТПЛ-10, coefficient - 150/5, in two phases

  - Vacuum circuit breaker: BB / TEL 10-20 / 630 with protection and control equipment. Nominal voltage - 10 kV. Rated current - 630 A.

  - Relay protection: use REST-02 type relay.

  - Voltage limiter: OPN / TEL in all three phases.

  - Power Zero-sequence current transformer: ТЗРЛ-150

- Must be new, in service

- Warranty: 2 years

- Must submit: Certificates of compliance with the standard of used equipment, factory measurement protocols (on circuit breakers and power transformers)

- Delivery time: 45 days

- Purchase of power cells for 800 kW motors in the 6 kV voltage distribution device of the pumping station "Bakhtrioni"

- (Size (cm)

  - Height: 230 (± 5)

  - Width: 100 (± 5)

  - Depth: 100 (± 5)

- The distribution box should be equipped with the following devices:

  - Jump switch: 6-10 kV voltage, 400 amps

  - Power transformer: ТПЛ-10, coefficient - 100/5, in two phases

  - Vacuum circuit breaker: BB / TEL 10-20 / 630 with protection and control equipment. Nominal voltage - 10 kV. Rated current - 630 A.

  - Relay protection: use REST-02 type relay.

  - Voltage limiter: OPN / TEL in all three phases

  - Zero-sequence current transformer: ТЗРЛ-150

- Must be new, in service

- Warranty: 2 years

- Delivery time: 45 days

- Certificates of compliance with the standard of used equipment, factory measurement protocols (on circuit breakers and power transformers)

- 630 kW capacity transformer substation with 1000 kW capacity transformer substation located at "Funicular I" pumping station.

Transformer substation settings and parameters:

- Capacity: 1000 kW

- Nominal voltage on high voltage side: 6 kV

- Switching device on high voltage side – 1

  - Load breaker: ВНАП 10 / 630-20-У2 - 1 piece

- Nominal voltage on the low voltage side: 0.4 kV

- Switching device on low voltage side -1

- Power automatic circuit breaker: Siemens 1600a - 1 piece

- Power transformer:

- Capacity: 1000 kW

- Voltage: 6 / 0.4 kV

- Scheme and connection group: Y / Y 0

- Automatic circuit breakers for 0.4 kV output lines (rated current, total quantity) - Siemens 630a (regular) - 3 pieces

- High voltage switch set - 3 pieces (6 kV)

- Power transformer: 2000/5 - 3 pieces

- Voltage and current control devices: Yes, all three phase voltage control

- High voltage guard: rated current - 140 A, - 3 pieces

- Must be new, in service

- Warranty: 3 years

- Certificates of compliance with the standard of used equipment, factory measurement protocol (on power transformer)