Rehabilitation of Wastewater Treatment Plant and New Sludge Treatment Facilities Gardabani

Functional Design Script

Rev 03

| 03 | Revision after tel-co | 22.03.2018 | TOI/SOF |
| --- | --- | --- | --- |
| 02 | In acc. to workshop 20.11.2017 in Munich | 21.12.2017 | Frindi |
| 01 | In acc. to workshop 29.09.2017 in Munich | 09.10.2017 | Frindi |
| Rev. | Change | Date | Name |

Content

0.	General description	6

1.	Inlet Chamber (035)	7

1.1	General description	7

1.2	Characteristics	7

1.3	Functional process description	7

1.4	Operation modi	8

2.	Admission building (060)	9

2.1	General description	9

2.2	Characteristics	9

2.3	Functional process description	9

2.4	Operation modi	10

2.5	Set point values	10

2.6	Control	11

3.	PU Coarse Screen (061)	12

3.1	General description	12

3.2	Characteristics	12

3.3	Functional process description	12

3.4	Operation modi	13

3.5	Set point values	14

3.6	Control	14

4.	Fine Screen Building (065)	15

4.1	General description	15

4.2	Characteristics	15

4.3	Functional process description	15

4.4	Operation modi	16

4.5	Set point values	16

4.6	Control	17

5.	Fine Screen (PU 066)	18

5.1	General description	18

5.2	Characteristics	18

5.3	Functional process description	19

5.4	Operation modi	19

5.5	Set point values	20

5.6	Control	21

6.	Aerated Grit and Grease Removal combined with high loaded aeration tank A-stage (070)	22

6.1	General description	22

6.2	Characteristics	23

6.3	Functional process description	23

6.4	Operation modi	25

6.5	Set point values	26

6.6	Control	27

7.	Distribution Well PST (105)	28

7.1	General description	28

7.2	Characteristics	28

7.3	Functional process description	28

7.4	Operation modi	28

7.5	Set point values	29

7.6	Control	29

8.	Primary Sedimentation Tanks (111, 112, 113, 114, 115)	30

8.1	General description	30

8.2	Characteristics	30

8.3	Functional process description	31

8.4	Operation modi	31

8.5	Set point values	32

9.	Outlet Channel (200)	33

9.1	General description	33

9.2	Characteristics	33

9.3	Functional process description	33

9.4	Operation modi	33

9.5	Set point values	33

10.	Primary sludge pumping station (object 120) + Return sludge pumping station (object 125)	34

10.1	General description	34

10.2	Characteristics	34

10.3	Functional process description	35

10.4	Operation modi	36

10.5	Set point values	39

10.6	Control	39

11.	Digested sludge pumping station (object 315) + Return sludge pumping station for PST 115 (object 320)	40

11.1	General description	40

11.2	Characteristics	40

11.3	Functional process description	40

11.4	Operation modi	41

11.5	Set point values	43

11.6	Control	43

12.	Primary Sludge Thickener (260) + PU Picket Fence (261)	44

12.1	General description	44

12.2	Characteristics	44

12.3	Functional process description	44

12.4	Operation modi	45

12.5	Set point values	46

12.6	Control	46

13.	Thickened Primary Sludge pumps (265)	47

13.1	General description	47

13.2	Characteristics	47

13.3	Functional process description	47

13.4	Operation modi	47

13.5	Set point values	48

13.6	Control	48

14.	Aerobic Digester (310)	49

14.1	General description	49

14.2	Characteristics	49

14.3	Functional process description	50

14.4	Operation Modi	50

14.5	Set point values	52

15.	Sludge Machinery Station (410)	53

15.1	General description	53

15.2	Characteristics	53

15.3	 Functional process description	54

15.4	Operation modi	54

15.5	Set point values	55

15.6	Control	56

16.	Precipitation Station (350)	57

16.1	General description	57

16.2	Characteristics	57

16.3	Functional process description	57

16.4	Operation modi	58

16.5	Set point values	58

16.6	Control	59

17.	Flocculant Station (360)	60

17.1	General description	60

17.2	Characteristics	60

17.3	Functional process description	61

17.4	Operation mode	61

17.5	Set point values	62

17.6	Control	62

18.	Air Purification Pre-Thickener (270)	63

18.1	General description	63

18.2	Characteristics	63

18.3	Functional process description	63

18.4	Operation modi	63

18.5	Control	64

19.	Air Purification Aerobic Digester (370)	65

19.1	General description	65

19.2	Characteristics	65

19.3	Functional process description	65

19.4	Operation modi	65

19.5	Control	66

20.	Process water booster station (390)	67

20.1	General description	67

20.2	Characteristics	67

20.3	Functional process description	67

20.4	Operation modi	67

20.5	Set point values	68

20.6	Control	68

21.	Dewatering Pumping Station (300)	69

21.1	General description	69

21.2	Characteristics	69

21.3	Functional process description	69

21.4	Operation modi	69

21.5	Set point values	70

21.6	Control	70

0.	General description	6

1.	Inlet Chamber (035)	7

1.1	General description	7

1.2	Characteristics	7

1.3	Functional process description	7

1.4	Operation modi	8

2.	Admission building (060)	9

2.1	General description	9

2.2	Characteristics	9

2.3	Functional process description	9

2.4	Operation modi	10

2.5	Set point values	10

2.6	Control	11

3.	PU Coarse Screen (061)	12

3.1	General description	12

3.2	Characteristics	12

3.3	Functional process description	12

3.4	Operation modi	13

3.5	Set point values	14

3.6	Control	14

4.	Fine Screen Building (065)	15

4.1	General description	15

4.2	Characteristics	15

4.3	Functional process description	15

4.4	Operation modi	16

4.5	Set point values	16

4.6	Control	17

5.	Fine Screen (PU 066)	18

5.1	General description	18

5.2	Characteristics	18

5.3	Functional process description	19

5.4	Operation modi	19

5.5	Set point values	20

5.6	Control	21

6.	Aerated Grit and Grease Removal combined with high loaded aeration tank A-stage (070)	22

6.1	General description	22

6.2	Characteristics	23

6.3	Functional process description	23

6.4	Operation modi	25

6.5	Set point values	26

6.6	Control	27

7.	Distribution Well PST (105)	28

7.1	General description	28

7.2	Characteristics	28

7.3	Functional process description	28

7.4	Operation modi	28

7.5	Set point values	29

7.6	Control	29

8.	Primary Sedimentation Tanks (111, 112, 113, 114, 115)	30

8.1	General description	30

8.2	Characteristics	30

8.3	Functional process description	31

8.4	Operation modi	31

8.5	Set point values	31

9.	Outlet Channel (200)	32

9.1	General description	32

9.2	Characteristics	32

9.3	Functional process description	32

9.4	Operation modi	32

9.5	Set point values	32

10.	Primary sludge pumping station (object 120) + Return sludge pumping station (object 125)	33

10.1	General description	33

10.2	Characteristics	33

10.3	Functional process description	34

10.4	Operation modi	35

10.5	Set point values	37

10.6	Control	38

11.	Digested sludge pumping station (object 315) + Return sludge pumping station for PST 115 (object 320)	39

11.1	General description	39

11.2	Characteristics	39

11.3	Functional process description	39

11.4	Operation modi	40

11.5	Set point values	42

11.6	Control	43

12.	Primary Sludge Thickener (260) + PU Picket Fence (261)	44

12.1	General description	44

12.2	Characteristics	44

12.3	Functional process description	44

12.4	Operation modi	45

12.5	Set point values	46

12.6	Control	46

13.	Thickened Primary Sludge pumps (265)	47

13.1	General description	47

13.2	Characteristics	47

13.3	Functional process description	47

13.4	Operation modi	47

13.5	Set point values	48

13.6	Control	48

14.	Aerobic Digester (310)	49

14.1	General description	49

14.2	Characteristics	49

14.3	Functional process description	50

14.4	Operation Modi	50

14.5	Set point values	52

15.	Sludge Machinery Station (410)	53

15.1	General description	53

15.2	Characteristics	53

15.3	Functional process description	54

15.4	Operation modi	54

15.5	Set point values	55

15.6	Control	56

16.	Precipitation Station (350)	57

16.1	General description	57

16.2	Characteristics	57

16.3	Functional process description	57

16.4	Operation modi	58

16.5	Set point values	58

16.6	Control	59

17.	Flocculant Station (360)	60

17.1	General description	60

17.2	Characteristics	60

17.3	Functional process description	61

17.4	Operation mode	61

17.5	Set point values	62

17.6	Control	62

18.	Air Purification Pre-Thickener (270)	63

18.1	General description	63

18.2	Characteristics	63

18.3	Functional process description	63

18.4	Operation modi	63

18.5	Control	64

19.	Air Purification Aerobic Digester (370)	65

19.1	General description	65

19.2	Characteristics	65

19.3	Functional process description	65

19.4	Operation modi	65

19.5	Control	66

20.	Process water booster station (390)	67

20.1	General description	67

20.2	Characteristics	67

20.3	Functional process description	67

20.4	Operation modi	67

20.5	Set point values	68

20.6	Control	68

21.	Wastewater Pumping Station (300)	69

21.1	General description	69

21.2	Characteristics	69

21.3	Functional process description	69

21.4	Operation modi	69

21.5	Set point values	69

21.6	Control	70

# General description

The subsequent document contains the functional design of the WWTP Gardabani.

The following plant components will be described:

- Inlet Chamber (object 035)

- Admission Building (object 060)

- PU Coarse Screen (object 061)

- Fine Screen Building (object 065)

- PU Fine Screen (object 066)

- Aerated Grit and Grease Removal combined with High Loaded Aeration Tank A-stage (object 070)

- Distribution Well PST (object 105)

- PST 1 (object 111)

- PST 2 (object 112)

- PST 3 (object 113)

- PST 4 (object 114)

- PST 5 (object 115)

- Outlet Channel (object 200)

- Primary Sludge Pumping Station (object 120)

- Return Sludge Pumping Station (object 125)

- Digested sludge Pumping Station (object 315)

- Return Sludge Pumping Station (object 320)

- Primary Sludge Thickener (object 260)

- PU Picket Fence (object 261)

- Thickened Primary Sludge Pumping Station (object 265)

- Aerobic Digester (object 310)

- Machinery Station (object 410)

- Precipitation Station (object 350)

- Polymer Station (object 360)

- Air purification Pre-Thickener (object 270)

- Air purification Aerobic Digester (object 370)

- Potable Water Booster Station (object 390)

- Wastewater Pumping Station (object 300)

# Inlet Chamber (035)

## General description

The incoming wastewater enters to the wastewater treatment plant at the Inlet Chamber (object 035).

In front of inlet chamber a new shaft (object 030) will be built. This shaft will be constructed around existing inlet concrete pipe DN 3300 mm as well as steel pipe DN 1200, while both pipes are still in operation. The new shaft will also be connected to four smaller inlet pipes and to a new temporary bypass (DN 2200 mm) for bypassing screens plants and grit chambers. For details please see separate document for temporary works.

## Characteristics

The chamber connect:

Main Collector 1: 	Tbilisi, Rustavi, Gardabani 1 Concrete Pipeline Dia. 3,300 mm

Main Collector 2: 	Nitrogen Steel Pipeline Dia. 1,200 mm

Industrial 1: 		Power Plant Steel Pipeline Dia. 245 mm

Industrial 2: 		Power Plant Steel Pipeline Dia. 245 mm

Collector: 			Gardabani 2 Steel Pipeline Dia. 325 mm

New temporary Bypass 	Dia. 2,200 mm

## Functional process description

After finalising the shaft object 030, the bypass DN 2200 and its connection to the existing transport sewer in direction to existing distribution chamber for eastern sedimentation tanks the existent pipe DN 3300 will be demolished inside the shaft and waste water will be routed via the new bypass. The opening to existing inlet chamber will be closed temporary with a steel-plate. This works will be done during a limited period. During this period incoming flow will be stopped and small flows from leaking will be pumped with temporary pumps. After sealing the steel-plate all downstream works can be done without being influenced by incoming waste water. When all works for the rehabilitation are completed, the steel-plate will be removed and the temporary bypass will be closed and removed. Afterwards the new plant is in operation.

Each inlet will be equipped with flow measurement (035MF001 - 005) delivered by the Employer.

The inlet chamber (object 035) is equipped with a level measurement (035ML001).

In the inlet chamber pH-value (035MQ001) and temperature (035MT001) will be measured and transferred to SCADA system. The data is for information purposes only.

The effluent flows by gravity to the distribution chamber between the Admission Building (object 060) and the inlet chamber. It distributes the water to the coarse screens and bypass channels of the screens. The distribution chamber possesses a coupling (035HH001) for scum removal.

## Operation modi

Normal operation

The sensors (035MF001 - 005) measure the inlet flow.

The sensor (035ML001) measures the water level in the Inlet Chamber.

The sensor (035MQ001) measures pH-value.

The sensor (035MT001) measures temperature.

Malfunction

If a sensor is broken, a new one has to be installed.

# Admission building (060)

## General description

Five coarse screens will be installed in existing channels. All existing channels will be refurbished and three will serve in future as bypass. The screens, penstocks and conveyors will be installed in a new building to protect the installation against low temperature, storm and rain. Each of the five screen channels can be isolated by a penstock. The screen building is equipped with a hoisting system.

The building is equipped with ventilation fan for additional ventilation. The ventilator is controlled by local room thermostat.

The enclosure is equipped with gas leakage detector to alarm if the H2S value or CO2 value or CH4 value rise above normal values. Sound and visual alarms are provided outside the enclosure to warn the operators if CO2, CH4 and H2S atmosphere occur. In this case entering of the screen building is not allowed.

## Characteristics

Installed aggregates:

Coarse screen 			5 pcs

Bypass channel			3 pcs

Belt conveyor 			2 pcs

Rotatable conveyor 		1 pcs

Container				2 pcs

Traveling beam			1 pcs

Ventilation fan:			1 pcs

## Functional process description

The coarse screens, bypass channels, and conveyors are enclosed in the building. Waste air is collected and transferred by forced ventilation (060AL101) to atmosphere.

The building is equipped with gas leakage detectors to alarm if the CH4, Benzine, Benzol value (060MQ001) or H2S value (060MQ002) or CO2 value (060MQ003) rise above a first limit (low values). Sound and visual alarms are provided outside the enclosure to warn the operators if CO2, CH4 and H2S atmosphere occur.

An overhead lifting device (060AH001) is provided in the building to allow the removal/maintenance of installed equipment.

## Operation modi

Normal operation

The sensor (060MQ001) measures the CH4, Benzine and Benzol concentration.

The sensor (060MQ002) measures the H2S concentration.

The sensor (060MQ003) measures the CO concentration.

For gas alarm, the fan is operated and guarantees a five fold turnover rate of the building.

Malfunction

If a sensor measures a predefined set point value max, an alarm is set and the ventilation fan start running to reach a five (5) fold turnover rate.

In case of a malfunction of the ventilation fan, a fault report is set .The fan has to be repaired. In this case entering of the screen building is not allowed.

If a sensor is broken, a new one has to be installed.

## Set point values

-	Concentration measurements

CH4, Benzine and Benzol detector (060MQ001)

Set point 060/11: Level Max. 1:		Gas warning, 20 % LEL

Set point 060/12: Level Max. 2:		Gas alarm, 40 % LEL

H2S detector (060MQ002)

Set point 060/13: Level Max. 1:		Gas warning, 20 % LEL, 4 ppm

Set point 060/14: Level Max. 2:		Gas alarm, 40 % LEL, 8 ppm

CO detector (060MQ003)

Set point 060/15: Level Max. 1:		Gas warning, 10 ppm

Set point 060/16: Level Max. 2:		Gas alarm, 30 ppm

-	Thermostat (060MT101)

Set point 060/21: controls room temperature	approx. 35 - 40 °C in summer

## Control

All switchboards for equipment in coarse screen house, fine screen house and sand removal are located inside a MCB building next to the fine screen building (object 960).

# PU Coarse Screen (061)

## General description

Five mechanically raked coarse screens, with a gap width of 20 mm are installed to separate rough material out of the incoming wastewater. If level difference up- and downstream a screen reaches a preselected level, the screen will start operation. The material retained on the screens is unloaded on belt conveyors in direction containers. Two screenings container with volume 4 m³ are located outside the building. The coarse screens, belt conveyor and penstocks are installed inside a building.

The daily amount of screenings in the coarse screens is calculated with 5 l/(PE x a) and 358,000 inhabitants. The daily screenings quantity is calculated to approx. 5 m³/d of wet screenings. For the dimensioning of the transport system the peak flow is chosen to 
4 m³/h.

To avoid smell leaks screens channels are covered.

## Characteristics

Design Coarse Screen:

Number of screens in operation:		4 pcs

Number of stand-by screens:			1 pcs

Capacity, each:				7,050 m³/h

Space between bars:			20 mm

Width of bars:				8 mm

Width of chamber:			1.40 m

Flow velocity in the screen:			1 m/s

Capacity of conveyor:			4.0 m³/h

Number of containers			2 pcs

Container volume			4.0 m³

## Functional process description

Five mechanically raked coarse screens (4 duty (061AK101 - 401) + 1 standby (061AK501)) are installed. The screens are designed to remove solids greater than 20 mm. The screenings are automatically transported by two belt conveyors (061AC001/002) and a rotatable belt conveyor (061AC003). The material is dropped into containers (060HK001/002). Two screenings containers with 4 m³ each are foreseen for installation outside the building. The screen cleaning operation is controlled by the measurement of water levels upstream and downstream the screens (061ML101 - 105). If level difference reaches a preselected level a screen will start cleaning. The conveyor will start the band movement and approx. 1 minute after than the cleaning process ends the conveyor will stop. Conveyors are dimensioned for maximum 4 m³/h.

Each screen channel can be isolated with penstocks installed upstream of coarse screens (060AS101 - 105) and downstream of the fine screen channels (065AS101 - 105). Three emergency bypass channels around the coarse screens are designed in case of total failure of the electrical panel. This bypass channel starts upstream of coarse screens with a fixed overfall weir.

An overhead lifting device (060AH001) is provided in the building to allow the maintenance of installed equipment.

The roof of the admission building is designed to dismantle the metallic construction above the coarse screens to allow the transport of each screen outside the building in case a replacement will be necessary in the future.

## Operation modi

Normal operation

The water level upstream and downstream the coarse screen is measured by level measurements (061ML101 - 105). A predefined water level difference (approx. 10 cm) starts the cleaning operation of one screen (set point 061/11).

The screenings falls into the skip of the belt conveyor. Screens and conveyors are interlocked and work synchronously. The conveyors start operation shortly before the screens start. When the screens stop a pre-selected time sequence (30 seconds) later, the conveyors stop, too.

Above the screenings containers a level measurement (061ML106) will be installed. The level sensor measures the filling level of the container and allows the change of discharge point for coarse screenings.

Malfunction

In case of failure of one screen the channel will be isolated and the water flow automatically in front of the remaining screens. Four screens are capable to pass 100 % of the peak flow.

In case there is no operation signal from the conveyors, the screens will continue their operation and the screenings will fall to the floor if the disturbance of the conveyor persists for a long time.

Alternatively, the screens can be switched off and water will bypass the screen plant via channel and pipes to the aerated grit removal chamber.

In case of screens failure an alarm occurs and the local Package Unit Control Cabinet 061PU gives a signal to the Scada system and all engines of the corresponding automatic-group will be switched off. After repairing the failure, the predefined manual or automatic-function has to be reactivated on-site (manual-off-manual or automatic-off-automatic).

In case of a malfunction of a coarse screen, a fault report is set.

In case of a malfunction of a conveyor, a fault report is set.

If a sensor is broken, a new one has to be installed.

## Set point values

-	Level difference measurement (061ML101 * 105)

Range 0 - 5 m

Set point 061/11: Water level difference starting screen operation	0.10 m

Set point 061/12: Water level difference 	0.15 m

all screens are working continuously

Set point 061/13: Fixed time sequence 	10 min

for cleaning fine screen if set value 061/11 is not attained

Set point 061/14: Time delay stopping conveyors

after screen cleaning stops 	30 sec

Set point 061/15: Time delay stopping rotatable conveyor

after conveyors stop				30 sec

Set point 061/16: Filling level in containers	1.20 m

Set point 061/17: maximum level upstream coarse screens	xxxx m

The level difference and the time sequence to start operation of the coarse screens as well the time loop for the conveyors to stop after screen respectively conveyor operation are finished are adjustable. The filling level of containers to change discharge of screenings depends on container dimensions and is adjustable.

## Control

All switch boards for equipment in coarse screen house, fine screen house and sand removal are located inside a MCB building (object 960).

# Fine Screen Building (065)

## General description

The fine screens, conveyors, screenings press and containers are enclosed in the building. Five channels are used for the installation of fine screen with automatic mechanical operation. Three screen channels will be used for bypass the screening plant. The screen building is equipped with a hoisting system.

The building for the fine screens, conveyors, press with their screening containers ensure operation in freezing conditions. Fan heaters are provided and ensure 10 °C in the building when the weather is cold for a proper operating process.

The building is equipped additionally with ventilation fans for additional ventilation. The ventilators are controlled by local room thermostat.

A gas leakage detector is installed in this building. In this case entering of the screen building is not allowed.

## Characteristics

Installed aggregates:

Fine screen:			5 pcs

Bypass channel:			3 pcs

Conveyor:				2 pcs

Rotatable conveyor:		1 pcs

Screenings press:		1 pcs

Ventilation fan:			2 pcs

Heating air fan:			3 pcs

Traveling crane:			1 pcs

## Functional process description

Waste air is collected and transferred by forced ventilation (1 duty (065AL201), 1 standby (065AL202)) to atmosphere. The building is equipped additionally with fan heaters (065AL004 - 006) for heating and ensures 10 °C in the building when the weather is cold. The building is equipped with gas leakage detectors to alarm if the CH4, Benzine, Benzol value (065MQ001) or H2S value (065MQ002) or COvalue (065MQ003) rise above a first limit (low values). Sound and visual alarms are provided outside the enclosure to warn the operators if CH4, Benzine, Benzole, CO, or H2S atmosphere occur.

An overhead lifting device (065AH001) is provided in the building to allow the removal/maintenance of installed equipment.

The distribution chamber between the fine screen building (object 065) and the grit and grease removal (object 070) possesses a sampler (065AK001) for providing samples of waste water.

## Operation modi

Normal operation

The sensor (065MQ001) measures the CH4, Benzine and Benzol concentration.

The sensor (065MQ002) measures the H2S concentration.

The sensor (065MQ003) measures the CO concentration.

The ventilation fans (065AL201/202) operate alternating at a 2.5 fold turnover rate of the room. For gas alarm, both fans are operated and guarantees a five fold turnover rate of the building.

Malfunction

If a sensor measures a predefined set point value max, an alarm is set and both ventilation fans start running to reach a five (5) fold turnover rate.

In case of a malfunction of one ventilation fan, a fault report is set and the standby fan starts running. The fan has to be repaired.

In case of a malfunction of a heating air fan, a fault report is set. The fan has to be repaired.

If a sensor is broken, a new one has to be installed.

## Set point values

-	Concentration measurements

CH4, Benzine and Benzol detector (065MQ001)

Set point 065/11: Level Max. 1:	Gas warning, 20 % LEL

Set point 065/12: Level Max. 2:	Gas alarm, 40 % LEL

H2S detector (065MQ002)

Set point 065/13: Level Max. 1:	Gas warning, 20 % LEL, 4 ppm

Set point 065/14: Level Max. 2:	Gas alarm, 40 % LEL, 8 ppm

CO detector (065MQ003)

Set point 065/15: Level Max. 1:	Gas warning, 10 ppm

Set point 065/16: Level Max. 2:	Gas alarm, 30 ppm

-	Thermostat (065MT201)

Set point 065/21: controls room temperature	approx. 35 - 40 °C in summer

Set point 065/22: controls room temperature	approx. 10 °C on a colder days

-	Ventilation fan (065AL201/202)

Set point 065/31: operation time of a ventilation fan to change

duty and standby:		24 h

## Control

All switchboards for equipment in fine screen house, coarse screen house and sand removal are located inside a MCB building (object 960).

# Fine Screen (PU 066)

## General description

Downstream of the coarse screens units (object 061), the wastewater is distributed to five fine screens channels. All five channels are fitted with mechanically cleaned fine screens. Four screens are capable to pass 100 % of the peak flow. The Fine screens are designed to remove solids greater than 5 mm. The screen cleaning operation is controlled by the measurement of water levels before and after the screens.

The screenings are dropped into a screenings press with a washing facility following two conveyors. This reduces the volume of screenings and the organic matters are washed out from the screenings and back into the wastewater flow. Hence, the screenings are less problematic to handle. The screenings are automatically transported by the screening press towards a rotatable conveyor and dropped into containers.

The daily amount of screenings in the fine screens is calculated with 10 l/(PE x a) and 358,000 inhabitants. The daily screenings quantity is calculated to approx. 10 m³/d of wet screenings. For the dimensioning of the transport system the peak flow is chosen to 
4 m³/h. After pressing the screenings, the quantity will be approx. 5 m³/d.

To avoid smell leaks screens channels are covered.

## Characteristics

Design Fine Screen:

Number of screens in operation:		4 pcs

Number of stand-by screens:			1 pcs

Capacity, each:				7,050 m³/h

Space between bars:			5 mm

Width of bars:				3 mm

Width of chamber:			2.35 m

Flow velocity in the screen:			1 m/s

Design Screenings Press and Conveyors:

Number of screenings press:			1 pcs

Input capacity of screenings press:		6 m³/h

Number of conveyor:			2 pcs

Number of rotatable conveyor:		1 pcs

Capacity of conveyor:			6 m³/h

Capacity of emergency conveyor:		6 m³/h

Skip volume:				4 m³

Number of skips:				2 pcs

## Functional process description

Five (4 duty (066AK101 - 401) and 1 standby (066AK501)) parallel mechanically raked fine screens are installed. The screens are designed to remove solids greater than 5 mm. The screenings are automatically transported by two belt conveyors (066AC001/002) into one screening press (066AC101). From here, the material is dropped into containers (065HK001/002) by using a short rotatable belt conveyor (066AC003). Two screenings containers with 4 m³ each are foreseen for installation inside the building. The screen cleaning operation is controlled by the measurement of water levels upstream and downstream the screens (066ML101 - 105). If level difference reaches a preselected level a screen will start cleaning. The conveyor will start the band movement and approx. 1 minute after than the cleaning process ends the conveyor will stop. Also screen press starts operation and ends after a preselected time. During operation time of press the small rotatable band transports the pressed screenings into the preselected container. Presses and conveyors are dimensioned for maximum 6 m³/h.

Each screen channel can be isolated with penstocks installed upstream of coarse screens (060AS101 - 105) and downstream of the fine screen channels (065AS101 - 105). Three emergency bypass channels around the fine screens are designed in case of total failure of the electrical panel. This bypass channel starts upstream of coarse screens with a fixed overfall weir. The effluent water of the fine screen channels and the bypass channels flow to a distribution chamber upstream the Grit and Grease Removal Chamber (object 070).

## Operation modi

Normal operation

The water level in the channels upstream and downstream the fine screen plant is measured by level measurements (066ML101-105). A predefined water level difference (approx. 20 cm) starts the cleaning operation of one screen (set point 066/11).

The screenings fall in the skip of the screening conveyors (066AC001 - 002) and will be transported to the hopper of the screenings press. Screens, conveyors and press are interlocked and work synchronously. The conveyors starts operation shortly before the screens start. At the same moment, the screening press starts operation. When the screens stops a pre-selected time sequence (30 second) later, the conveyors stops, too, and the same time sequence (30 second) later the press stops operation.

Additional wash water is injected into the screenings through the hopper of the screening press. The wash water then absorbs and removes dissolvable organic matter from the screenings. The wash water will be drained into a sewer which ends upstream of the fine screens. Injection time of wash water is controlled by a runtime/pause switch in the local panel.

Above the screenings containers a level measurement (066ML106) will be installed. The level sensor measures the filling level of the container and allows the change of discharge point for coarse screenings.

Malfunction

In case of failure of one screen the channel will be isolated and the water flow automatically in front of the remaining screens. Four screens are capable to pass 100 % of the peak flow.

In case there is no operation signal from the press or conveyor, an alarm occurs and the screens will continue their operation. The operator has to remove the press and has to install a mobile screw conveyor (066AC004) located inside the fine screen building. The screenings will be discharged by help of the mobile screw conveyor into the rotatable conveyor then into the containers. In the meantime, until the mobile conveyor starts operation the operator has to discharge screenings manually into containers.

Alternatively, the screens can be switched off and water will bypass the screen via channel and pipes to the grit chamber.

In case of screens failure an alarm occurs and the local Package Unit Control Cabinet 066PU gives a signal to the Scada system and all engines of the corresponding automatic-group will be switched off. After repairing the failure, the predefined manual or automatic-function has to be reactivated on-site (manual-off-manual or automatic-off-automatic).

In case of a malfunction of a fine screen, a fault report is set.

In case of a malfunction of a conveyor, a fault report is set.

In case of a malfunction of the screenings press, a fault report is set.

If a sensor is broken, a new one has to be installed.

## Set point values

-	Level difference measurement (066ML101 - 105)

Range 0 - 3 m

Set point 066/11: Water level difference starting screen operation	0.15 m

Set point 066/21: Water level difference				0.20 m

all screens are working continuously

Set point 066/31: Fixed time sequence				10 min

for cleaning fine screen if set value 066/11 is not attained

Set point 066/41:	Set point level starting conveyors and press		0.15 m

Set point 066/51: Time delay stopping conveyors

after screen cleaning stops			30 sec

Set point 066/61: Time delay stopping screenings press

after conveyors stops				30 sec

Set point 066/71: Time delay stopping rotatable conveyor

after screenings press stops			30 sec

Set point 066/81: Filling level in containers	1.20 m

The level difference and the time sequence to start operation of the fine screens as well the time loop for the conveyors respectively screenings presses to stop after screen respectively conveyor operation are finished are adjustable. The filling level of containers to change discharge of screenings depends on container dimensions and is adjustable.

## Control

All switch boards for equipment in fine screen house, coarse screen house and sand removal are located inside a MCB building (object 960).

# Aerated Grit and Grease Removal combined with high loaded aeration tank A-stage (070)

## General description

The aerated grit chamber and grease trap are the first stage biological process, following the principals of an adsorption-activated-sludge-process (AB-process). The grit removal and the high loaded aeration tank are one unit. The combined function is biological treatment and sand plus grease removal.

Four grit and grease removal tanks will be constructed, each capable of handling 25% of the maximum flow under rainy conditions. Hydraulically even higher flows can be treated, but efficiency will decrease.

Grit will be removed in order to reduce the risk of damage to the mechanical equipment in the following treatment units, and grease will be removed to avoid non-aesthetic conditions caused by the volatile organics and malodorous floating sludge. The settled grit will be transported to the grit classifier then unloaded into a container. The retained grease will be scraped off and discharged into a grease collector shaft.

Highly loaded biological A-stage

The aerated grit chamber is calculated and proposed as a biological treatment (A-stage). The A-stage is a biological high loaded activated sludge stage. Aerobic and facultative anaerobic activated sludge is produced and pollutants can be removed by adsorbing and additionally by biodegradation. This operation has special advantages. The primary pollutants are adsorbed to the activated sludge flocs and will be removed by taking off primary sludge. This process is similar to the flocculants in a chemical enhanced primary sedimentation tank. The oxygen consumption is reduced.

The simultaneous use of an aerated grit chamber as an adsorption stage is achieved with additional air requirements and with a separate return sludge circle to activate growth of biomass and bioflocs for adsorption.

Aerated Grit and grease removal

A standing wave is produced with compressed air aeration on one side. The sands are separated on the tank floor. The average retention period is higher than 10 minutes and a sand removal for grit with a diameter bigger than 0.20 mm is realised. The scum is bloated with the fine bubble aeration and can be skimmed from the water surface. The bottoms of the activated sludge basins (aerated grit removal tank) are single-sided fitted with membrane diffusers to guarantee sufficient aeration capacity.

## Characteristics

The aerated grit removal combined with high-loaded aeration tank A-stage will meet the following requirements:

| Maximum flow under rainy weather conditions | 28,200 m³/h |
| --- | --- |
| Number of tanks | 4 pcs |
| Length, each | 50 m |
| Width, each | 4 m |
| Water depth up to | 5.59 m |
| Volume, each | 895 m³ |
| Volume, total | 3,580 m³ |
| DS-concentration | 1.5 - 2.0 g DS/l |
| BOD-volume load | < 10 kg BOD/(m³ x d) |
| Return sludge flow, max. | 2,664 m³/h |
| Grit pumps capacity 30 m³/h; mounted on scraper bridge | 4 pcs |
| Depth of air introduction | 4.85 m |
| Aeration capacity for biological treatment | 4,712 kg O2/d |
| Min. required air introduction per hour for grit elimination | 1,600 Nm³/h |
| Max. air demand per hour | 3,240 Nm³/h |
| Grit slurry pumps capacity 70 m³/h; feed of classifier | 2 pcs |
| Grit classifier capacity 70 m³/h | 1 pcs |
| Velocity scraper bridge | 4 m/min |
| Scraper running time | 25 min |
| Skip volume | 4 m³ |
| Number of skips | 2 pcs |

## Functional process description

To avoid settlement of suspended solids in the existing channel between fine screens and grit chamber an aeration pipe system with coarse bubble aeration (070HK010) will be installed. This system provides sufficient turbulence in the channel and increase the active volume of A-stage.

The wastewater from the distribution chamber of fine screens flows to the new combined aerated grit chambers and grease removal tanks. Each line of the grit and grease removal chamber is fitted with penstocks at the inlet (070AS101 - 401) and outlet (070AS102 - 402) side to allow isolation of a line for maintenance purposes.

The fine bubble aeration is performed by membrane plate diffusers (070HK070) which produce a vertical flow velocity (wave) for avoiding sedimentation of organic matter and provide sufficient efficiency for oxygen transfer. The compressed air is produced in the common blower station (object 410) located in building (object 350) for both A-stage and aerobic sludge stabilisation.

The aeration of the A-stage is ensured by

- average dissolved oxygen in inlet flow:	3,000 kg O2/d

- NOx-N-Inlet-load:			   413 kg/d

- Oxygen equivalent from NOx:		1,200 kg O2/d

- Aeration system	max:		3,240 Nm³/h

min:		1,600 Nm³/h

Dissolved oxygen in inlet flow, in NOx-loads and oxygen transfer at min aeration capacity (1,600 Nm³/h) ensures sufficient oxygenation capacity for biological treatment in A-stage. In dead minimum aeration for the wave in a grit chamber leads to increasing oxygen concentrations.

Aeration is automatically regulated by electrically actuated control valve (070AS070) based on measurement of the average oxygen concentration measured by the two oxygen transmitters (070MQ101 - 201) in the common outlet channel of the tanks. Alternatively, one of these metered DO- values by each individual sensor can be selected as input for control of the assigned regulation valve.

The blowers for aeration are controlled by the air pressure that fluctuates relative to the control valve openings. The pressure is measured in the transport air pressure pipes by a pressure sensor and transmitter (410MP104).

The sands are separated with both, a helical standing wave and a special cross section of the building. They are collected in a trough at the tank bottom.

The sand-water-mixture is pumped into 2 collecting channels (one for two trains) and transported through this channel to the pit with 2 grit slurry pumps. It will be then pumped by the 2 (1 duty (070AP501) + 1 standby (070AP502)) grit slurry pumps to the grit classifier (070AK001). A level measurement (070ML101) located in the grit collecting chamber controls the grit pump operation. The grit pumps will be interlocked with the grit classifier; the start of the pump causes the start of the grit classifier as well. The sand classifier separates the sand from the water on behalf of principle of gravity. The sand from the classifier is transported by screw conveyor to a container (070HK001/002). The container is able to accommodate 4 m³ of sand. Drainage water of the grit classifier is delivered to the effluent channel of fine screens (object 060) by gravity.

Scum, oil and grease is skimmed from the water surface by a blade, mounted on scraper bridge (070AK101 + 301), which transport the scum to a scum pipe and collects it in a grease collecting chamber at the outlet side of the grit removal tank. From there the grease will be sucked by a suction vehicle.

The waste water from four sand removal tanks passes a penstock at outlet of each tank and flows into a distribution chamber with a volume of approx. 300 m³. Additional dosing of precipitant is possible if CEPT operation is active. Dosing pumps located in the Technical building (object 350) dose via two dosing lines precipitant into the shafts in effluent Grit Chamber. Two fixed overflow weir divide the flow into 80 % and 20 %. The weirs can be separated by means of removable stop-logs. Smaller flow is directed into sedimentation tank No 115 and bigger flow is directed to the distribution chamber object 105 serving other four sedimentation tanks No 111 - 114.

## Operation modi

Normal operation

The sensor (070ML001) measures the water level in the distribution chamber at inlet side.

The sensor (070ML002) measures the water level in the distribution chamber at outlet side.

The sensors (070MQ101 - 201) measure the oxygen concentration in the outlet channel of the combined aerated grit and grease removal chamber and high loaded aeration tank.

The sensor (070ML101) measures the water level in the pump sump for feeding grit classifier.

The sensor (070MF001) measures the flow towards grit classifier.

Scraper bridge

Two tanks are fitted with a common scraper bridge. The scraper bridge removes sand and scum. The scraper bridge starts running from the park position at the influent side of the tank in direction to the outlet. Two submersible grit slurry pumps are installed at one bridge. During the movement to the end sand is pumped to a grit collecting channel, one channel per 2 trains. The sand-water-mixture flows by gravity from collecting channel to the common grit collecting pit. The scraper bridge will be interlocked with level in pit with grit transfer pumps. The grit transfer pump will be interlocked with the grit classifier; the start of the pump causes the start of the grit classifier as well. If the pump stops, the classifier keeps in operation for a predefined time sequence.

When reaching the end position of the tank the scum blade forms in a trough at the end of the tank and the scum will be evacuated towards the collecting pit.

After a pre-selected period the scraper changes his moving direction towards inlet. The sand pump is still working until the scraper bridge reaches the parking position at the inlet side of the tank. The scum blade will be lifted up and kept in the uplifted position while the scraper is running back to the inlet of the tank.

The scraper bridge operates cyclic time-controlled by package unit control cabinet. After a predefined time sequence (4 hours), the scraper starts running for a predefined amount of cycles. The scrapers are interlocked to each other because of capacity of grit classifier.

Pressured air system

The compressed air is produced by 3 blowers (2 duty + 1 stand-by), installed in the sludge machinery station (object 410) and delivered in a common delivery pipeline on the pressure side. This pipe will be distributed to two feeding lines, one for the aerated grit chamber incl. distribution channel and the other one for the aerobic stabilisation tank (object 310).

Aeration of combined grit chamber and A-stage is controlled by a control valve in the air feed line. The preselected DO-value of approx. 0.3 - 0.5 mg O2/l will be provided by opening and closing the regulation valve. As the system is sensitive, a time lag of approx. 30 seconds is foreseen in the Scada to prevent permanent operation of the regulation valve. Average value of the oxygen measurements (070MQ101-201) will be used for control loop. Alternatively, one of these metered DO- values by each individual sensor can be selected as input for control of the assigned regulation valve.

In every line five aeration grids each with 4 diffuser membrane plates are installed. Totally 80 diffuser membrane plates are installed, 20 pieces for each line. It is possible to isolate each of these grids by a ball valve in the drop pipe DN 50

Malfunction

If a line has been taken out of operation the relevant penstocks in both inlet and outlet channel must be closed. Malfunction may be in time of inspection, when a complete tank has to be emptied or when the membrane diffuser have reached their live time and must be exchanged.

In case of malfunction of a scraper bridge an alarm occurs and the local package unit control cabinet gives a signal to the Scada system and all engines of the corresponding automatic-group will be switched off. After repairing the failure, the predefined manual or automatic-function has to be reactivated on-site (manual-off-manual or automatic-off-automatic).

In case of malfunction of a grit slurry pump in grit and grease removal chamber a fault report is set.

In case of malfunction of the duty grit slurry pump in pump sump for grit chamber a fault report is set and the stand-by pump starts running.

In case of malfunction of the grit classifier, a fault report is set, a bypass system is foreseen and the grit can be routed by opening a gate valve (070HS001) via a flexible hose towards the existent grit storage area.

If a sensor is broken, a new sensor has to be installed.

## Set point values

Set point 070/11:		Predefined time sequence for a restart of scraper bridge approx. 4 h

-	Oxygen measurement (average of 2 measurements 070MQ101 - 201)

Range: 0 - 5 mg/l

Set point 070/21:		Pre selected DO-value in A-stage 		approx. 0.5 mg/l

Set point 070/22:		Predefined time sequence for a restart of air regulation valve

approx. 30 s

-	Level measurement (070ML101)

Range: 0 - 5 m

Set point 070/31:		Water level inside the pumping station, which starts operating pump (070AP501/502):					+ 2 m

Set point 070/32:		Grit classifier (070AK001) starts with operating pump (070AP501/502)

Set point 070/33:		Water level inside the pumping station, which stops operation pump (070AP501/502):					+ 0.7 m

Set point 070/34:		Follow up time for the Grit classifier (070AK001) to stop after grit-slurry pumps operation is finished:			180 sec

Set point 070/35:		Water level inside the pumping station, which stops pumps 
(070AP101 - 404) installed at scraper bridges:		+ 3.50 m

Set point 070/36:		Operation time of a pump to change duty and stand-by

The set point values which are visible in SCADA are changeable by the operator.

## Control

The control panel is located on the scraper bridge.

All switch boards for equipment in fine screen house and sand removal are located inside a MCB building (object 960).

# Distribution Well PST (105)

## General description

The distribution chamber is designed to distribute 80 % of the flow from the aerated grit to four PST´s (object 111 -112 -113 -114).

The outlets of the distribution tank are fitted each with 2 penstocks (105HS101 - 102 /

201 - 202 / 301 - 302 / 401 - 402) to isolate any primary sedimentation tank in case of malfunction.

The overfall walls have the same height and the same length. Thus results in a uniform flow to each primary sedimentation tank.

## Characteristics

Installed penstocks for isolation:	8 pcs

## Functional process description

The distribution chamber (object 105) collects wastewater from the distribution chamber at the downstream side of the grit and grease removal chamber (object 070). It receives 80 % of total flow and is designed to distribute the flow to four primary sedimentation tanks (PST 1 - 4, object 110).

Flocculant from the polymer station (object 360) is dosed into the wastewater. The overfall walls have the same height and the same length. Thus results in a uniform flow to each primary sedimentation tank. The four outlets of the distribution tank are fitted each with manually operated penstocks to isolate any clarifier in case of malfunction or maintenance.

The chamber is fitted with a level measurement (105ML101).

## Operation modi

Normal operation

An equal wastewater stream flows to every connected PST. All penstocks are full open.

Malfunction

In case of malfunction or maintenance, any clarifier can be isolated by penstocks.

If a sensor is broken, a new one has to be installed.

## Set point values

No set points are necessary.

## Control

No control is necessary.

# Primary Sedimentation Tanks (111, 112, 113, 114, 115)

## General description

The primary clarifiers remove readily settleable solids and floating materials and reduce the suspended solids content. The purpose of the primary clarifiers is to remove a substantial portion of the organic solids from the untreated wastewater, with a resulting decrease in the organic and solid loadings in effluent channel.

Treated wastewater will be discharged into outlet channel (unit 200).

Settled sludge on one hand will be pumped to the aerated unit chamber to activate a biological treatment process and to increase efficiencies of the mechanical treatment stage. On the other hand primary sludge will be pumped to the static thickener (object 260). Pumping stations and thickener will be submitted in a separate package incl. functional design script.

## Characteristics

| Dry weather flow | 480,581 m³/d |
| --- | --- |
| Backload sludge liquor | 853 m³/d |
| Total inlet flow | 481,434 m³/d |
| Number of primary clarifiers | 5 |
| Diameter | 49,5 m |
| Water depth, each | > 4.75 - 5.24 m |
| Volume, each | > 9,387 m³ |
| Total volume | > 47,110 m³ |
| Overfall weir loading | 344 m³/m/d |
| Retention time at dry weather flow | 2.41 h |

The retention time in the tanks results to:

tR,t = V/Q = 47,110 / 19,585 = 2.41 h at dry weather flow

The efficiency of the primary clarifiers depends on retention time, overflow weir loading and operation of A-stage. It is calculated as follows:

Following parameters are expected:

BOD5 				50 %	=> 23.0 mg/l

COD					50 %	=> 49.4 mg/l

Suspended solids:	75 %	=> 15.3 mg/l

Total nitrogen		17.5 %	=>   9.0 mg/l

P tot					30 %	=>   0.6 mg/l

The quantity of primary sludge is calculated to:

0.75 x 29,306 = 21,979 kg DS/d, 	with SS-content:	17 kg/m³

21,979 / 17 = 1,293 m³/d

## Functional process description

The feeding of the tanks occurs via a pipe (DN 2000) into the central structure. The outflow of the tanks occurs via effluent weirs (111HK101, 112HK201, 113HK301, 114HK401, 115HK501) mounted at the new steel effluent channels (111HK102, 112HK202, 113HK302, 114HK402, 115HK502) located at supports at outside wall of the tanks. The channels are equipped with scum boards. Treated wastewater will be discharged into the outlet channel (unit 200).

The scraper (111AK101, 112AK201, 113 AK301, 114AK401, 115AK501) collects the settled sludge into the central hopper of the primary clarifier. Scum is collected in a scum hopper (111HK103, 112HK203, 113HK303, 114HK403, 115HK503) served by the scum beam at scraper bridge. The scum from PST 111-114 is collected in a scum chamber located near the outside wall and flows by gravity towards the primary sludge pumping station (object 120). The scum from PST 5 flows into a shaft (object 400.4) located in between the PST 115 and the aerobic digester (object 310). The scum is mixed with the discharged stabilised sludge into the shaft (object 400.4) and gravitates directly to the digested sludge pumping station (object 315)

The sludge hoppers of PST 1,2,3 and 4 are connected via new sludge discharge pipes with the primary sludge pumping station (object 120). The sludge hopper of PST 5 is connected with the sludge pumping station (object 315).

The primary sedimentation tanks include following measurements:

-	Sludge level sensor (110ML101, 110ML201, 110ML301, 110ML401, 110ML501)

## Operation modi

Normal operation:

PST 1, 2, 3 and 4 are fed with the flow coming from the distribution well PST (object 105).

PST 5 is fed with the flow coming from shaft no. 3 (object 400.3).

The sensors (110ML101, 110ML201, 110ML301, 110ML401, 110ML501) measure the sludge levels.

The scrapers (111AK101, 112AK201, 113AK301, 114AK401, 115AK501) are working continuously.

Malfunction:

In case of failure of the scraper, a fault report is set.

If a sensor is broken, a new sensor has to be installed.

If a sludge level is higher than a preset value (variable set point in SCADA) a fault report is set.

## Set point values

-	Sludge level sensor (110ML101, 110ML201, 110ML301, 110ML401, 110ML501)

-	Range: 0 – 5 m

Set point 111 – 115/11:				i. e. 1 m

# Outlet Channel (200)

## General description

The outlet channel (object 200) collects treated wastewater to discharge.

## Characteristics

Channel is equipped with level, flow and pH measurements and a sampler.

Dimensions:

Width = 3.00 m

Height = 2.83 – 2.96m

Capacity:	max. 73.80 l/s ≅ 28,188 m³/h

## Functional process description

The outlet channel (object 200) collects the treated wastewater from the effluent channels of all primary sedimentation tanks 111 - 115.

The outlet channel includes:

-	Level measurement (200ML002)

-	Flow measurement (200MF001)

-	pH measurement (200MQ001) and Temperature measurement (200MT001)

-	Sampler (110AK001)

The flow in the outlet channel goes to discharge.

## Operation modi

Normal operation:

The sensors are installed in the channel and measure water level, flow and pH values.

The sampler assays.

Malfunction:

If a sensor is broken, a new sensor has to be installed.

If the sampler is broken, a new sampler has to be installed

## Set point values

No set point is necessary.

# Primary sludge pumping station (object 120) + Return sludge pumping station (object 125)

## General description

The primary sludge pumping station (object 120) consist of two pumping units. The primary sludge pumps (object 120) for primary sludge from PST units 111 - 114 (object 110) and the return sludge pumps (object 125) from PST units 111 - 114 (object 110).

For evacuation of water a cellar evacuation pump (120AP002) is foreseen which starts automatic operation in case of leakage detected by a level switch (120ML101). The pump is installed in existing pump sump.

A ventilation fan (120AL001) provides an air exchange. The station is equipped additionally with a fan heater (120AL005) for heating and ensures 10 °C in the building when the weather is cold. The ventilators are controlled by local room thermostat (120MT001).

A Lifting facility allows the removal of the pumps.

## Characteristics

Primary sludge pumping station:

Daily operation time per pump:			16 h

Primary sludge quantity:				88.4 m³/h

Number of pumps in operation:			2 pcs

Number of stand-by pumps:				1 pcs

Necessary capacity of each pump:			44.2 m³/h

Chosen capacity of each pump:			80 m³/h

Chosen head of pumps:				15 m

Return sludge pumping station (PST 111 - 114):

Due of total flow:					80 %

Return sludge quantity, Max.:			2,131 m³/h

Daily operation time per pump:			24 h

Number of pumps in operation:			1 pcs

Number of stand-by pumps:				1 pcs

Chosen capacity of each pump:			2,140 m³/h

Chosen head of pumps:				7.8 m

## Functional process description

Object 125:

The sludge hoppers of PST 111 - 114 (object 110) are connected via sludge discharge pipes DN 300 with the primary sludge pumping station (object 120). At each sludge discharge pipe, an electrical actuated valve (120AS101 - 120AS401) is installed. This pumping station consist also the return sludge pumping station (object 125), equipped with 2 centrifugal pumps (one duty (125AP101) + one standby (125AP201)) as return sludge pumps to the combined A- Stage and grit and grease removal chamber (object 070).

The return sludge pumps (125AP101/201) are controlled by frequency converters.

A pre-selected return sludge ratio (13.6 % at dry weather flow) calculates the necessary return sludge flow. The calculation is done with an average inlet flow, measured by a flow measurement (200MF001), over 1 h time period multiplied with the given ratio. The return sludge flow is measured by a flow measurement (125MF001). The four electric actuated gate valves (120AS101 - 120AS401) in the sludge pipelines from the sludge hopper of the tanks are open and the flow measurement (125MF001) regulate the calculated flow. 80 % of total return sludge flow will be pumped by installed pump capacity.

Object 120:

The sludge hoppers of PST 111 - 114 (object 110) are connected via sludge discharge pipes with the primary sludge pumping station (object 120). At each sludge discharge pipe, an electrical actuated valve (120AS101 - 120AS401) is installed. Furthermore scum from primary sedimentation is routed to the pumping station. The four separate sludge discharge pipes are connected to a header located at the suction side of both pumping stations (object 125) and (object 120).

The primary sludge pumping station (unit 120) is connected to the suction header of the return sludge pumping station (object 125). The primary sludge pumping station will be equipped with three dry-installed rotary lobe pumps (two duty (120AP101/201) + one standby (120AP301)). Each primary sludge pump possesses an overpressure switch (120MP101 - 301) and a temperature sensor (120MT101 - 301) as protection device. The pipes are fitted with all necessary valves. The primary sludge will be conveyed by the rotary lobe pumps to the primary sludge thickener (object 260). The primary sludge flow is measured and recorded (120MF101). The daily quantity of primary sludge is approx. 1,415 m³/d in design flow conditions.

The control program for primary sludge pumping can be selected based on pre-selected base value of daily sludge quantity (e.g. 1,400 m³/d). The set point value of daily sludge quantity is calculated with the following formula.

QPS = 1,400 m³/d + SSA-stage x VA-stage / SSRS

| Volume VA-stage | 3,580 m³ |
| --- | --- |
| SSRS -content | measured by dry solids sensor (120MQ101) |
| SSA-stage | (SSA-stage – SSset value) |
| SSset value | 1.6 g/l |
| SSA-stage | determined in laboratory |

The pressure pipe towards sludge thickener (object 260) is fitted with a measurement (120MQ101), which analyses dry solids content. This sensor measures the DS-content value in return sludge.

Example

| Volume VA-stage | 3,580 m³ |
| --- | --- |
| SSRS -content | 17 g/l |
| SSset value | 1.6 g/l |
| SSA-stage | 1.8 g/l |
| SSA-stage | 0.2 g/l = 1.8 – 1.6 |

QPS = 1,400 m³/d + SSA-stage x VA-stage / SSRS

QPS = 1,400 m³/d +  x 3,580 / 17

QPS = 1,400 + 42 m³/d

The Operator makes every workday a manual control of DS-concentration in laboratory and SCADA system will calculate automatically the amount of the daily sludge quantity to be withdrawn. The daily sludge quantity is designed to be pumped in 18 h uniformly distributed over 24 h towards the sludge thickener (object 260). The daily primary sludge quantity will be pumped by help of a Start – Pause mode.

Daily operation time per pump QPS = 1,442 m³/d / (2 x 80 m³/h) = 9 h

Alternatively manually controlled constant flow of primary sludge can be selected by operator, if the above mentioned automatically operation mode is not possible for operation.

## Operation modi

Normal operation

Object 125:

The pumping station is operated automatically. The return sludge pumps are controlled by the flow measurement (125MF001). The return sludge flow from the primary sedimentation (unit 111-114) is nearly continuously and flows to the pumping station suction header. The flow sensor will increase or decrease the inverter of the pumps to maintain a predefined flow.

The cycling between the pumps will be done automatically when a pre-selected operation time has elapsed. The operational status of the pumps is monitored by the SCADA system.

For pump start at least one electric valve (120AS101 - 401) must be open.

Object 120:

The primary sludge pumps are operated automatically. A pre-selected daily sludge quantity will be pumped by use of a Start – Pause mode. The primary sludge flow is measured and recorded (120MF101).

The cycling between the pumps will be done automatically when a pre-selected operation time has elapsed. The operational status of the pumps is monitored by the SCADA system.

Malfunction

In order to prevent the discharge pipe DN 300 of each PST from blocking a flushing system using the primary sludge pumps is designed. For this reason, the primary sludge pressure pipe is connected at two places with the header at the suction side of the pumping stations (object 120 and 125). The primary sludge evacuation towards the primary sludge thickener (object 260) will be rerouted into the suction header and can be used to flush each underground pipe between the sludge hoppers in PST and the pumping station (object 120). Necessary gates valves (120HS081 and 120HS082) are provided in the flushing pipes and must open manually. In normal operation, both gate valves (120HS081 and 120HS082) are closed.

Flushing operation PST 111

For flushing the underground pipe between PST 111 and the primary sludge pumping station (object 120) one primary sludge pump (120AP101 / 201 / 301) will be operated and the listed valves have to be hold in following position:

Gate valve 120HS072:		closed (manually)

Gate valve 120HS081:		open (manually)

Gate valve 120HS082:		closed (manually)

Gate valve 120HS091:		closed (manually)

Gate valve 120HS092:		open (manually)

Gate valve 120AS101:		open

Gate valve 120AS201:		open

Gate valve 120AS301:		open

Gate valve 120AS401:		closed (electrically)

Flushing operation PST 114

For flushing the underground pipe between PST 114 and the primary sludge pumping station (object 120) one primary sludge pump (120AP101 / 201 / 301) will be operated and the listed valves have to be hold in following position:

Gate valve 120HS072:		closed (manually)

Gate valve 120HS081:		open (manually)

Gate valve 120HS082:		closed (manually)

Gate valve 120HS091:		closed (manually)

Gate valve 120HS092:		open (manually)

Gate valve 120AS101:		closed (electrically)

Gate valve 120AS201:		open

Gate valve 120AS301:		open

Gate valve 120AS401:		open

Flushing operation PST 112

For flushing the underground pipe between PST 112 and the primary sludge pumping station (object 120) one primary sludge pump (120AP101 / 201 / 301) will be operated and the listed valves have to be hold in following position:

Gate valve 120HS072:		closed (manually)

Gate valve 120HS081:		closed (manually)

Gate valve 120HS082:		open (manually)

Gate valve 120HS091:		open (manually)

Gate valve 120HS092:		closed (manually)

Gate valve 120AS101:		open

Gate valve 120AS201:		open

Gate valve 120AS301:		closed (electrically)

Gate valve 120AS401:		open

Flushing operation PST 113

For flushing the underground pipe between PST 113 and the primary sludge pumping station (object 120) one primary sludge pump (120AP101 / 201 / 301) will be operated and the listed valves have to be hold in following position:

Gate valve 120HS072:		closed (manually)

Gate valve 120HS081:		closed (manually)

Gate valve 120HS082:		open (manually)

Gate valve 120HS091:		open (manually)

Gate valve 120HS092:		closed (manually)

Gate valve 120AS101:		open

Gate valve 120AS201:		closed (electrically)

Gate valve 120AS301:		open

Gate valve 120AS401:		open

In case of a malfunction of a pump, a fault report is set and the standby pump starts running.

In case of a malfunction of an electric actuated gate valve, a fault report is set.

In case of a leakage detected by level switch an alarm is set and the evacuation pump (120AP002) starts running.

## Set point values

Object 120:

-	Flow measurement (120MF101)

-	Range: 1 – 3,000 m³/d

Set point 120/11:	chosen daily quantity of primary sludge	1,415 m³/d

Set point 120/12:	operation time of an aggregate to change

duty and standby:			24 h

-	Dry solid concentration measurement (120MQ101)

Range: 1 - 50 g/l

Set point 120/21: Set point dry solids content:	1.6 g DS/l

-	Thermostat (120MT001)

Range: 0 - 50 °C

Set point 120/31: Set point level full capacity:		approx. 35 °C

-	Level measurement (120ML101)

Range: 0 – 1 m

Set point 120/41:	Set point level evacuation pump

starts running:			0.20 m

Object 125:

-	Flow measurement (120MF101)

Range: 0 - 2500 m³/h

Set point 125/11: Return sludge range between:	 	1,630 - 2,140 m³/h

Set point 125/21:	Operation time of an aggregate to change

duty and standby:			24 h

The set point values which are visible in SCADA are changeable by the operator.

## Control

The control panels for the pumps are located in MCB above the pumping station (unit 120).

# Digested sludge pumping station (object 315) + Return sludge pumping station for PST 115 (object 320)

## General description

The Digested sludge pumping station (object 315) consist of two separated pumping unit. The return sludge pumps (object 320) for return sludge of PST 115 (object 110) and another the digested sludge pumps (object 315) for digested sludge from the aerobic digester (object 310).

For evacuation of water a cellar evacuation pump (315AP002) is foreseen which starts automatic operation in case of leakage detected by a level switch (315ML101). The pump is installed in existing pump sump.

A ventilation fan (315AL001) provides an air exchange. The station is equipped additionally with a fan heater (315AL006) for heating and ensures 10 °C in the building when the weather is cold. The ventilators are controlled by local room thermostat (315MT001).

A Lifting facility allows the removal of the pumps.

## Characteristics

Return sludge pumping station for PST 115 (object 320):

Due of total flow:					20 %

Return sludge quantity:				max. 533 m³/h

Daily operation time per pump:			24 h

Number of pumps in operation:			1 pcs

Number of stand-by pumps:				1 pcs

Chosen capacity of each pump:			535 m³/h

Chosen head of pumps:				7.8 m

Digested sludge pumping station (object 315):

Daily operation time per pump:			16 h

Digested sludge quantity:				28.8 m³/h

Number of pumps in operation:			1 pcs

Number of stand-by pumps:				1 pcs

Number of spare pumps :				1 pcs

Chosen capacity of each pump:			40 m³/h

Chosen head of pumps:				10 m

## Functional process description

Object 320:

The sludge hopper of PST 115 (object 115) is connected via a sludge discharge pipe DN 300 with the return sludge pumps (object 320). At the sludge discharge pipe, electrical actuated valve (320AS501) is installed.

The return sludge pumping station (object 320) will be equipped with two dry-installed pumps (one duty (320AP301) + 1 standby (320AP401)). The return sludge pumps are controlled by frequency converters.

A pre-selected return sludge ratio (13.6 % at dry weather flow) calculates the necessary return sludge flow. 20 % of total return sludge flow will be pumped by installed pump capacity to the combined A- Stage and grit and grease removal chamber (object 070).

Object 315:

The aerobic digester (object 310) is connected via a sludge discharge pipe DN 250 with the shaft 400.4 upstream of the digested sludge pumps (object 315). Furthermore scum from primary sedimentation tank PST 115 gravitates to the shaft 400.4 and will be mixed with digested sludge. At the sludge discharge pipe from shaft 400.4 towards the digested sludge pumping station an electrical actuated valve (315AS601) is installed. The digested sludge pumping station will be equipped with two dry-installed pumps (one duty (315AP401) + 1 standby (315AP501)). One spare pump (315AP601) will be provided. Each digested sludge pump possesses an overpressure switch (315MP101/201) and a temperature sensor (315MT101/201) as protection device. A flow meter (315MF601) and a dry matter sensor (315MQ601) is installed in the collector pressure pipe. The flow meter shall primarily serve to register sludge volume transported. Both sensors are registered in the Scada. The digested sludge flows to the existent sludge drying beds (object 520).

In the suction header pH-value (315MQ002) and temperature (315MT002) will be measured and transferred to SCADA system. The data is for information purposes only.

## Operation modi

Normal operation

Object 315:

The pumping station is operated automatically. The digested sludge pumps are controlled by a level sensor (400.4ML101) installed inside the shaft (object 400.4) located between the aerobic digester (object 310) and the primary sedimentation tank (object 115).

As the aerobic digester is a flow-through-tank, digested sludge according to the inlet raw sludge quantity spills over an installed overflow into a pipe directing the digested sludge by gravity via a shaft 400.4 to the digested sludge pumping station (unit 315) via opened draw off electrical actuated valve (315AS601).

In the suction header pH-value (315MQ002) and temperature (315MT002) will be measured and transferred to SCADA system. The data is for information purposes only.

The pumps are operated in an alternating sequence in order to minimise the wear of the pumps. The cycling between the pumps will be done automatically when a pre-selected operation time has elapsed.

Object 320

The pumping station is operated automatically. The return sludge flow from the primary sedimentation (object 115) is nearly continuously and flows to the pumping station suction header.

The pumps are operated in an alternating sequence in order to minimise the wear of the pumps. The cycling between the pumps will be done automatically when a pre-selected operation time has elapsed. The operational status of the pumps is monitored by the SCADA system.

For pump start electric valve (320AS501) has to be open.

Malfunction

Flushing operation

In order to prevent the discharge pipe DN 300 of PST (object 115) from blocking a flushing system using the digested sludge pumps (315AP401 / 315AP501) is designed. For this reason, the digested sludge pressure pipe is connected with the header at the suction side of the return sludge pumping station (object 320). The digested sludge evacuation towards the existent sludge drying beds (object 520) will be rerouted into the suction header of the return sludge pumps and can be used to flush the underground pipe between the sludge hopper in PST 115 and the pumping station (object 320). Necessary gates valves (315HS020 and 315HS030) are provided in the flushing pipe respectively in the pressure pipe towards the drying beds. During flushing works the gate valve (315HS020) must be closed manually and the gate valve (315HS030) installed in the flushing pipe must be opened manually. Furthermore, electrically actuated valve (320AS501) must be closed. In normal operation, gate valve (315HS020) and (320AS501) are open and (315HS030) is closed.

Flushing operation PST 115

For flushing, the underground pipe between PST 115 and the return sludge pumping station (object 320) one digested sludge pump (315AP401 / 315AP501) will be operated and the listed valves have to be hold in following position:

Gate valve 315HS020:		closed (manually)

Gate valve 315HS030:		open (manually)

Gate valve 320AS501:		closed (electrically)

In case of a malfunction of a pump, a fault report is set and the standby pump starts running. Furthermore, one digested sludge spare pump (315AP601) will be provided.

In case of a malfunction of an electric gate valve, a fault report is set.

In case of a leakage detected by level measurement an alarm is set and the evacuation pump (315AP002) starts running.

## Set point values

Object 315:

-	Flow measurement (315MF601)

Range: 1 – 1,500 m³/d

Set point 315/11: chosen daily quantity of digested sludge	461 m³/d

Set point 315/12:	operation time of an aggregate to change

duty and standby:			24 h

-	Level measurement (400.4ML101)

Range: 0 – 5 m

Set point 315/21: Level min. (stop operating pumps):	+ 295.20

Set point 315/22: Level max. in shaft 400.4:		+ 297.30

Set point 315/22: Level max and a fault report is set:		+ 297.40

-	Dry solid concentration measurement (315MQ601)

Range: 1 - 50 g/l

Set point 315/31: Set point dry solids content:		38 g DS/l

-	Thermostat (315MT001)

Range: 0 - 50 °C

Set point 315/41: Set point level full capacity:		approx. 35 °C

-	Level measurement (315ML101)

Range: 0 – 1 m

Set point 315/51:	Set point level evacuation pump

starts running:			0.2 m

Object 320:

Set point 320/11: Return sludge range between:	 	410 - 535 m³/h

Set point 320/12:	operation time of an aggregate to change

duty and standby:			24 h

The set point values which are visible in SCADA are changeable by the operator.

## Control

The control panels for the pumps are located in MCB above the pumping station (unit 120).

# Primary Sludge Thickener (260) + PU Picket Fence (261)

## General description

The primary sludge of the A-stage is gravitationally thickened. The thickener is a "continuous flow" type with diameter of 20 m equipped with a picket fence and with fixed overflow weir for the removal of sludge liquor. The thickener will be constructed as a circular concrete tank with its base sloping towards a bottom hopper located in the centre of the tank.

The feeding pipe ends in height of the water level at the centre of the tank. The sludge "draw-off" is installed at the bottom of the hopper. Inside the thickener, a sludge blanket level sensor is installed.

The thickener is covered. The foul air under the covered tank will be sucked and transferred to biofilter (unit 270).

## Characteristics

Max. quantity of primary sludge (1.7 % DS):	1.414 m³/d

Max. quantity of thickened sludge (5.0 % DS):	   461 m³/d

The following dimensions were chosen:

Amount:				1 unit

Diameter:			20.00 m

Surface:				314 m²

Total depth:		4.60 m

Volume:				1.445 m³

Hydraulic retention time:	1.0 d

Sludge retention time:	3.0 d

## Functional process description

Primary sludge of the primary sedimentation tanks (object 110) is pumped via rotary lobe pumps located in the Primary sludge pumping station (object 120) to the Primary Sludge Thickener (object 260). The feeding pipe ends in height of the water level at the centre of the tank. The thickener receives the flow and solids in the sludge settle down. A picket fence (261AM101) stirs the sludge continuously. Inside the thickener a sludge blanket level sensor (260ML101) is installed. As the gravitational thickener is a flow-through-tank, sludge liquor according to the inlet raw sludge quantity spills over an installed overflow weir (260HK101) into a pipe directing the sludge liquor by gravity to the distribution chamber between fine screen (object 065) and grit and grease removal (object 070). The thickened sludge is drawn off via a pipe at the bottom of the hopper to the thickened primary sludge pumps (object 265). For monitoring of pH-value a sensor (265MQ002) is installed in the discharge pipe from the sludge thickener towards the thickened sludge pumping station. Both pH- and temperature (265MT002) will be measured and transferred to SCADA system. The data is for information purposes only.

Waste air is delivered to a biofilter (object 270) for treatment.

## Operation modi

Normal operation

The thickener is a “continuous flow” type. This results in a continuous working picket fence (261AM101).

The sludge blanket level sensor (260ML101) controls the operation of the rotary lobe pumps (265AP101 - 201) located in the thickened sludge pumping station (object 265).

A sludge level approx. 0.20 m higher than a pre-selected level approx. 3.80 m will start the pumps operation. 30 cm below this level the pump stops operation. The suction pipe is fitted with a dry solid measurement (265MQ001). A dry solid minimum value of approx. 4.5 % corresponds to a minimum sludge blanket level which stops the evacuation pumps. A maximum dry solid value of approx. 5.0 % will correspond to maximum sludge blanket level which starts the evacuating pumps.

The thickened sludge evacuation pumps with a capacity of 40 m³/h, each, are designed as (1 + 1) stream solution. The daily sludge quantity is designed to be pumped in 16 h uniformly distributed over 24 h towards the aerobic digester. Each pump has an overpressure switch (265MP101/201) to protect the pump, when a pressure pipe is blocked. Additionally, the pumps are fitted with temperature sensor (265MT101/201) as protection device.

Downstream of the pumps a flow measurement device (265MF001) is located to measure the quantity of thickened primary sludge towards the aerobic digester.

Upstream of the pumps a pH sensor (265MQ002) is installed to monitor the pH value of thickened sludge.

The pipes can be flushed by using the up- and downstream installed flushing devices.

The local package unit control cabinet (261PU) for the picket fence is installed at thickener’s service bridge. The control panel for the pumps is located inside a MCB building (object 960).

Malfunction

In case of malfunction of the picket fence (261AM101) the DS-concentration will decrease. The function of the thickener may continue but the retention time of sludge in the digesters will decrease. A fault report is set.

Alternatively, the primary sludge thickener will be bypassed and primary sludge will pass to the aerobic digestion. A bypass with necessary fittings is foreseen. The gate valve (260HS261) in the feed pipe of thickener must close, the gate valve (265HS015) at the pump discharge pipe must close and the valve (265HS270) in the bypass line must open. The thickened sludge pumps stop during bypass of the thickener.

In case of malfunction of the sludge blanket sensor (260ML101) a fault report is set.

In case of malfunction of the sludge blanket sensor the evacuation pumps can be operated manually depending on experience and a manual identified sludge level in the thickener. Dry solids sensor (265MQ001) helps to identify the sludge level blanket.

If a sensor is broken, a new one has to be installed.

## Set point values

-	Sludge blanket level measurement (260ML101)

Range 0 - 5 m

Set point 260/11: Pre selected sludge blanket level inside the tank to start the drawn off thickened sludge pumps			approx. 0.20 m

Set point 260/12: Pre selected sludge blanket level inside the tank to stop the drawn off thickened sludge pumps			approx. 0.30 m

Set point 260/13:	Pre selected sludge blanket level inside the tank 	approx. 4.0 m

The set point values which are visible in SCADA are changeable by the operator.

## Control

The local package unit control cabinet (261PU) for the picket fence is installed at thickener’s service bridge. The control panel for the pumps is located in MCB inside the new building (unit 960).

# Thickened Primary Sludge pumps (265)

## General description

The thickened sludge pumps are designed as (1 + 1) stream solution. The pumps transport sludge from the Primary sludge Thickener (object 260) to the Aerobic Digester (object 310).

## Characteristics

Daily operation time per pump:		16 h

Number of pumps in operation:		1 pcs

Number of stand-by pumps:			1 pcs

Chosen capacity of each pump:		40 m³/h

Chosen head of pumps:			20 m

## Functional process description

Thickened sludge is drawn off by 2 pumps (1 duty (265AP101) + 1 standby (265AP201)) installed in object 265. The withdrawal pipe is fitted with a dry solid measurement (265MQ001), which together with the sludge blanket level sensor (260ML101) stops or starts the evacuation pumps. A sludge level approx. 0.20 m higher than a pre-selected level approx. 4.0 m will start the pumps operation. 30 cm below this level the pump stops operation. The suction pipe is fitted with a dry solid measurement (265MQ001). A dry solid minimum value of approx. 4.5 % corresponds to a minimum sludge blanket level which stops the evacuation pumps. A maximum dry solid value of approx. 5.0 % will correspond to maximum sludge blanket level which starts the evacuating pumps.

Each pump has an overpressure switch (265MP101/201) and a temperature sensor (265MT101/201) as protection device. On the common pressure pipe of the pumps a flow measurement device (265MF001) is located to measure and record the quantity of thickened primary sludge towards the aerobic digester. The pipes can be flushed by using the up- and downstream installed flushing devices.

## Operation modi

Normal operation

The sensor (260ML101) measures the sludge blanket level in the primary sludge thickener (object 260).

The sensor (265MQ001) measures the dry solid concentration in the withdrawal pipe.

The sensor (265MQ002) measure the pH value in the withdrawal pipe.

The sensor (265MF001) measures the sludge flow to the aerobic digester (object 310).

The sensors (265MT101/201) measure the temperature of the pumps.

The sensors (265MP101/201) measure the pressure on pump pressure side.

Malfunction

In case of malfunction of the sludge blanket sensor the evacuation pumps will be operated manually depending on experience and a manual identified sludge level in the thickener. Dry solids sensor helps to identify the sludge level blanket.

The primary sludge thickener can be bypassed and primary sludge will pass to the aerobic digestion. A bypass with necessary fittings is foreseen. The gate valve (260HS261) in the feed pipe of thickener must close, the gate valve (265HS015) at the pump discharge pipe must close and the valve (265HS270) in the bypass line must open. The thickened sludge pumps stop during bypass of the thickener.

In case of malfunction of one thickened sludge pump, the corresponding feed and evacuation pipeline will be locked using the corresponding two valves and emptied by using the installed flushing devices. A fault report is set and the stand-by pump starts running.

## Set point values

-	Sludge blanket level measurement (260ML101)

Range 0 - 5 m

Set point 260/11: Pre selected sludge blanket level inside the tank to start the drawn off thickened sludge pumps			approx. 0.20 m

Set point 260/12: Pre selected sludge blanket level inside the tank to stop the drawn off thickened sludge pumps			approx. 0.30 m

Set point 260/13:	Pre selected sludge blanket level inside the tank 	approx. 4.0 m

-	Dry solid measurement (265MQ001)

Set point 265/21:	Pre-selected dry solid concentration in the thickener

effluent stop the pumps			approx. 45 kg/m³

The set point values which are visible in SCADA are changeable by the operator.

## Control

The control panel for the pumps is located in MCB inside the new building (unit 960).

# Aerobic Digester (310)

## General description

Sludge is stabilised in aerobic sludge digester. On the flat bottom a fine bubble aeration system will be installed.

A tank with defoaming agent and a dosing pump will be installed in chemical dosing building (object 350). The defoaming agent can be dosed into sludge feed line to the stabilisation tank. The stabilisation tank is covered with a plastic membrane textile and waste air will be extracted and treated in one biofilter. To prevent foam discharge to the biofilter a sprinkler system next to the waste air removal will be installed. The spraying equipment is connected to the potable water network (unit 390).

The aerated tank is equipped with a fixed overflow for the removal of digested sludge. The sludge flows in a shaft (object 400.4) which serves as pump sump for the 2 digested sludge pumps located in object 315. From this pumping station (object 315) sludge is pumped to existing sludge drying beds (object 520).

## Characteristics

Tank-volume:				9,430 m³

Retention time max:			24 d

Retention time min:			20.4 d

Thickened sludge:			461 m³/d

|  |  | Unit | Total |
| --- | --- | --- | --- |
| a | access of raw sludge | kg SS/d | 23,066 |
| b = a x 0.85 | average access of raw sludge | kg SS/d | 19,606 |
| c = a x 0.75 | organic contingent from raw sludge | kg oSS/d | 17,300 |
| d = b x 0.75 | average organic contingent from raw sludge | kg oSS/d | 14,705 |
| e | quantity of sludge, thickened | m³/d | 461 |
| f = e x 0.85 | average quantity of sludge, thickened | m³/d | 392 |
| g = c x 0.30 | max. reduction of the oDS load | kg oSS/d | 5,190 |
| h = d x 0.30 | average reduction of the oDS load | kg oSS/d | 4,411 |
| i = a - g | total DS after stabilisation, max. | kg SS/d | 17,876 |
| j = b - h | total DS after stabilisation in average | kg SS/d | 15,195 |
| k = (c - g) / i | organic rate | - | 0.68 |
| l = i / e | ratio of particulate material of digester sludge | kg/ m³ | 38,8 |

## Functional process description

The aerobic digester (object 310) is fed by sludge from the thickened primary sludge pumps (object 265). Before entering the digester, defoaming agent from the tank for defoaming agent (340HK001) can be dosed into the sludge feed line by two dosing pumps (one duty (340AP101) + 1 standby (340AP201)).

Pressurised air from the sludge machinery station (object 410) is delivered to the Aeration system (310HK310).

The digester is equipped with three combined oxygen and temperature sensor (310MQ101 / 310MT101), (310MQ102 / 310MT102) and (310MQ103 / 310MT103) and a level sensor (310ML101).

Digested sludge flows through a drowned pipe to a shaft (object 400.4). The shaft serves the digested sludge pumping station (object 315).

Waste air is delivered to a biofilter (object 370) for treatment. To prevent foam transport towards the biofilter, a sprinkling system (310HK311) is installed on the top of the sludge level. The sprinkler system is fed with potable water. The potable water pipe is fitted with an electric actuated butterfly valve (310AS312). The spraying equipment for the digester will be switched on automatically by opening the electric actuated butterfly valve. The operation time is recorded in Scada. The operation time must be limited to prevent higher water inflow und thus reduction of the retention time.

## Operation Modi

Normal operation:

For a working sprinkling system the butterfly valve 310AS312 has to be open (by operator at SCADA or on site).

The sensors (310MQ101 / 102 / 103) measure the oxygen concentration.

The sensors (310MT101 / 102 / 103) measure the temperature.

The sensor (310ML101) measures the level.

Pressured air system

The compressed air is produced by 3 blowers (2 duty + 1 stand-by), installed in the sludge machinery station (object 410) and delivered in a common delivery pipeline on the pressure side. This pipe will be distributed to two feeding lines, one for the aerated grit chamber incl. distribution channel (object 070) and the other one for the aerobic stabilisation tank (object 310).

Aeration of aerobic stabilisation tank is controlled by a control valve (310AS310) in the air feed line. The preselected DO-value (310MQ101 / 102 / 103) of approx. 0.5 mg O2/l will be provided by opening and closing the regulation valve. As the system is sensitive, a time lag of approx. 30 seconds is foreseen in the Scada to prevent permanent operation of the regulation valve.

Average value of the oxygen measurements (310MQ101 / 102 / 103) will be used for control loop. Alternatively, one of these metered DO- values by each individual sensor can be selected as input for control of the assigned regulation valve.

Ensuring sufficient mixing is done by preselected minimum air flow to the stabilisation tank. Additionally a pulse aeration could be chosen to increase mixing power. Details are described in operation modes of the blower station (object 410).

Defoaming agent:

Start-up

Defoaming agent is fed into the sludge feed line. At start-up a quantity of 0.2 % defoaming agent in relation to the SS-Load of the sludge in the digester is feed in a period of three days. This concludes the following initial dosing rate:

SS-Load:			9.430 m³ x 38.8 kg/m³ = 365.400 kg SS

Initial dosing rate:	365.400 kg SS x 0.2 % / 3 d = 243.6 kg/d

=10.1 kg/h

Normal operation

At daily operation a quantity of 0.2 % defoaming agent is dosed in relation to the daily sludge feed:

Daily dosing rate:		23.066 kg SS/d x 0.2 % 	= 	46	kg/d

=	1.9	kg /h

Malfunction:

If the water level reaches a preset value (set value 310/11, variable set point in SCADA) the feeding pump (265AP101 / 201) stops and a fault report is set. The operator has to check the status of the evacuation pump (315AP401 / 501).

In case of malfunction of the defoaming agent dosing pump a fault report is set and the standby pump starts running.

In case of malfunction of the butterfly valve 310AS312 a fault report is set.

If a sensor is broken, a new sensor has to be installed.

## Set point values

-	Level measurement (310ML101)

-	Range:	0 - 6.0 m

Set point 310/11:	Maximum level in digester to stop feeding pumps 265AP101/201

and alarm is set:					5.00 m

Set point 310/12:	Level min:					4.90 m

-	Measurement oxygen concentration (310MQ101 / 102 / 103)

-	Range:	0 - 5 mg/l

Set point 310/21:	Set point O2:	0.5 mg/l

Set point 310/22:	Set point min:	0.3 mg/l

Set point 310/23:	Set point max:	2.0 mg/l

# Sludge Machinery Station (410)

## General description

The pressured air for aerobic sludge stabilisation (object 310) and for A-stage is produced in the sludge machinery station (object 410). Inside the sludge machinery station three turbo blowers are installed in a separate room.

The turbo blowers are designed for 6,500 Nm³/h, each with a pressure difference of 650 mbar. The air demand is calculated for a fine bubble aeration system in the stabilisation tank. For details please see process calculation.

The blower capacities are adequate to keep the minimum oxygen concentration in the stabilisation tanks at 0.5 mg/l minimum.

The blower units aerating the sludge stabilisation stage are monitored through pressure, temperature and flow sensors and registered in the Process Control System (PCS). The amount of air delivered to the sludge stabilisation is adjustable from the Process Control System (PCS).

## Characteristics

Peak demand per hour in the sludge stabilisation is calculated to:

αOC20°C ≅ 336 kg O2/h and air demand of approx. 6,828 Nm³/h

An aeration system with fine bubble diffusers and transfer factor α = 0.5 is chosen.

In A-stage, peak demand per hour is calculated to approx. OC20°C = 196 kg O2/h and air demand of total 3,240 Nm³/h.

Total required capacity of 2 duty blowers is minimum 6,828 + 3,240 = 10,067 Nm³/h. The provided duty blowers has a total air production of 2 x 6,500 = 13,000 Nm³/h.

Additional ventilation for cooling of blower station is installed.

| Installed blower capacity | 3 x 6,500 Nm³/h |
| --- | --- |
| Installed blower power | 3 x 149,5 kW |
| Active blowers | 2 |
| Back-up units | 1 |
| Pressure difference | 650 mbar |
| Mixing power input | 16 W/m³ - 32 W/m³ |
| Ventilator for cooling | 2 units, 6,000 m³/h each |

## Functional process description

The blowers will operate fully automatically based on a pre-set oxygen value monitored in the aerobic sludge stabilisation reactor and directly based on the air pressure in the header air pressure pipe.

The blowers are autonomous and locally controlled. Set point for the oxygen is controlled via the SCADA system and monitoring of the blowers is also done by the SCADA system.

All turbo blowers (2 duty (410AV201, 410AV202), 1 standby (410AV203)) deliver the air in a common header on the pressure side.

The header includes:

-	Flow measurement (410MF101) in line to aerobic digester (object 310)

-	Pressure measurement (410MP104)

-	Temperature measurement (410MT104)

The flow measurement (410MF101) in the feed line to aerobic digester and three oxygen measurements (310MQ101 / 310MQ102 / 310MQ103) in the aerobic digester (object 310) controls the quantity of the pressured air, which has to be delivered by the turbo blowers. On one hand to ensure sufficient mixing and on the other hand to ensure sufficient oxygenation.

The SCADA will control the operation times of all blowers to be similar by changing duty and assist automatically.

A thermostat (410MT001) inside the blower building controls the ventilators (410AL001 and 410AL002) for ventilation of the blower room.

## Operation modi

Normal operation:

The sensor (410MP104) measures the pressure in the header pipe.

The sensor (410MT104) measures the temperature in the header pipe.

The sensor (410MF101) measures the airflow in the feed pipe of the digester.

The sensor (410MT001) measures the temperature in the blower building.

The minimum air demand of the aerobic stabilisation for mixing is i.e. 6,500 Nm³/h. To ensure the air demand two blowers have to operate. The butterfly valve (410HS201, 410HS202, 410HS203) are open under normal conditions. The blowers will operate fully automatically based on a preset pressure value (set value 410/31) based on the pressure sensor (410MP104) in the header pipe.

Both ventilators for air-cooling (410AL001 / 410AL002) starts working based on a preset temperature value (set value 410/51) of thermostat (410MT001) in the building.

Malfunction:

In case of malfunction of one air blower, a fault report is set and the standby blower starts running. Each blower pressure pipe can be blocked by installed butterfly valves.

If a sensor is broken, a new sensor has to be installed.

## Set point values

-	Measurement oxygen concentration (310MQ101 / 102 / 103) in digester

-	Range:	0 - 5 mg/l

Set point 410/11: Frequency control of blowers:	approx. 1.0 mg O2/l

Set point 310/21:	Set point O2:	0.5 mg/l

Set point 310/22:	Set point min:	0.3 mg/l

Set point 410/23:	Set point max:	2.0 mg/l

-	Pressure Measurement (410MP104)

Set point 410/31:	Pressure in header: 		600 mbar

range: 550 - 650

Set point 410/32:	Minimum pressure: 		530 mbar

range: 500 - 600

Set point 410/33:	Maximum pressure: 		630 mbar

range: 580 - 650

-	Flow measurement (410MF101)

Set point 410/41:

Minimum air flow to aerobic digester: 6,500 Nm³/h

range: 3,500 - 8,000 Nm³/h

Set point 410/42:

Maximum air flow to aerobic digester: 7,000 Nm³/h

range: 6,500 - 10,000 Nm³/h

Set point 410/43:

Preselected time between 2 cycles of pulse aeration:	24 h (range 1 - 168 h)

Set point 410/44:

Duration of pulse aeration:			  5 h (range 1 - 60 Min.)

Set point 410/45:

Chosen air flow for pulse aeration:			11,000 (range 9,000 - 13,000)

-	Thermostat (410MT001)

Set point 410/51: approx. 35 °C is full capacity

The set point values which are visible in SCADA are changeable by the operator.

## Control

Control panels are located in a separate chamber adjacent to object 350.

Control of blowers depends on:

-	oxygen sensor in object 310:	310MQ101-310MQ102-310MQ103

-	oxygen sensor in object 070:	070MQ101-070MQ201

-	flow measurement to object 310:	410MF101

Aerobic digester has to be aerated for ensured mixing with minimum air flow. If measured flow is too low or too high, frequency of blowers must increase or decrease.

If measured oxygen concentration is below set value 410/11 set value 410/42 is chosen as set point for air flow and for control of blowers.

If measured oxygen concentration is higher than set value 410/21 set value 410/41 is chosen as set point for air flow and for control of blowers.

# Precipitation Station (350)

## General description

The ferric chloride dosing plant is a stand-alone plant started from a signal from the treatment works control system with the ability to accept a signal to pace the dosing pumps in response to flow through the WWTP Outlet channel.

Storage tank for the ferric chloride is located indoors, frost free and are isolated in a separate frame to protect from accidental leakage.

The ferric chloride is dosed into the two outlet shafts of the grit chambers (object 070) to the distribution chambers of the primary sedimentation tanks in proportion to their respective waste water flow rate.

## Characteristics

Coagulants

Storage capacity reach 	14 d

Storage capacity (1 Tank)	25 m³

Capacity of Dosing Pumps

No. of Dosing Pumps	PST 111 - 114 	1 pcs

No. of Standby Pumps			1 pcs

Chosen capacity of each pump		200 l/h

Chosen head of pumps			10 m

No. of Dosing Pumps	PST 115 		1 pcs

No. of Standby Pumps			1 pcs

Chosen capacity of each pump		40 l/h

Chosen head of pumps			10 m

## Functional process description

The precipitant tank (350HK101) is fit with level sensors (350ML101 - 350ML102 - 350ML103).

Four precipitant dosing pumps deliver the ferric chloride to the outlet shafts of the grit and grease removal (object 070). Two of these precipitant dosing pumps (1 duty (350AP101), 1 standby (350AP102)) deliver the ferric chloride to the shaft at grit chamber, which is feeding PST 111 - 114 (object 110) via the distribution chamber (object 105). This line includes a flow sensor (350MF101). The other two dosing pumps (1 duty (350AP201) and 1 standby (350AP202)) deliver the ferric chloride to the shaft at grit chamber, which is feeding PST 115 (object 110) via the connecting shaft (object 400.3). This line includes a flow sensor (350MF501).

## Operation modi

Normal operation:

The sensors (350ML101 - 350ML102 - 350ML103) measures the level in the precipitant tank.

The sensors (350MF101 and 350MF501) measure the flow.

The control of dosing will be done automatically or manual.

Two possible operating modes are foreseen:

-	The precipitation flow rate is calculated in proportion to the discharge flow in the outlet channel (object 200). In case of rain weather (Qoutlet > 19,858 m³/h) the proportional dosing rate shall be limited (Set point 350/11). Dosing rate is controlled to be proportional to the outlet flow measured by the flow sensor (200MF001) in object 200.

-	If requested by process conditions or during maintenance the precipitation dosing rate can be adjusted manually independently from WWTP outlet flow (Set point 350/12)

Malfunction:

In case of a minimum level (set point 350/13, variable set point in SCADA) in the precipitant tank, a fault report is set and the dosing pumps are stopped.

In case of malfunction of a duty dosing pump, a fault report is set and the standby pump will start automatically.

If a sensor is broken, a new sensor has to be installed.

## Set point values

-	Flow Measurement (350MF101 and 350MF501)

-	Range:	0 - 200 l/h

Set point 350/11: 	Range

Automatic proportion Qprecipitant dosing / Qoutlet :

Dosing rate [%] = Qprecipitant dosing / Qoutlet x Dosing Factor

| Interval | Qoutlet | Dosing Factor |
| --- | --- | --- |
| 1 | < 19,585 m³/h | 0 - 1 |
| 2 | 19,585 - 28,188 m³/h | 1 - 0,5 |

Set point 350/12:

PST 111 - 114 	(80 %)	Precipitation flow rate 0 - 200 l/h

PST 115	(20 %)	Precipitation flow rate 0 - 40 l/h

Set point 350/13:

Minimum precipitant level value:	= 0.5 m

(Operator has to order new precipitant)

The set point values which are visible in SCADA are changeable by the operator.

## Control

Control panels are located in a separate chamber adjacent to object 350.

# Flocculant Station (360)

## General description

The polymer preparation system is designed as an automatic preparation plant for polymer powder. The storage for the polymer powder is designed for the consumption of 10 days. The polymer solution shall be dosed into the distribution wells of the primary sedimentation tanks (object 111 - 115) in proportion to their respective wastewater flow rate. Flocculant station is equipped with totally four dosing pumps. Two redundant dosing pumps are provided for each of their dosing lines.

## Characteristics

Flocculant - Powder Polymer

Storage capacity		10 d

Storage capacity		5 m³

Estimated dosing ratio 	1.0 g reagent / m³ inflow

Polyelectrolyte-plant

Chambers			3 pcs

Retention time		1 h

Volume				2.8 m³

Post-dilution

Post-dilution using potable water		0.1 %-dilution

Potable water for post-dilution			28.2 m³/h

Capacity of dosing pumps

No. of Dosing Pumps	PST 111 - 114 	1 pcs

No. of Standby Pumps			1 pcs

Chosen capacity of each pump		2.8 m³/h

Chosen head of pumps			20 m

No. of Dosing Pumps	PST 115 		1 pcs

No. of Standby Pumps			1 pcs

Chosen capacity of each pump		1.0 m³/h

Chosen head of pumps			20 m

Capacity of dosing line

PST 111 - 114 		80 %	DN 80	24.8 m³/h

PST 115			20 %	DN 40	6.2 m³/h

## Functional process description

Powder polymer from the powder polymer dosing station (360AC001) is mixed with potable water from potable water booster station (object 390) in the preparing tank. The tank is equipped with three mixers (360AM101 - 360AM103) and four level sensors (360ML001 - 360ML004).

Two polymer dosing pumps (1 duty (360AP101), 1 standby (360AP201)) deliver the polymer to the distribution chamber of PST 111 - 114 (object 105). The other two polymer dosing pumps (1 duty (360AP301), 1 standby (360AP401)) deliver the polymer to the Shaft No. 3 (object 400.3). Each pump is equipped with a temperature sensor (360MT101 - 360MT401) and a pressure sensor (360MP101 - 360MP401) as protection device. Downstream of the pumps a flow sensor (360MF101, 360MF501) is designed for each line. Each stream has a dilution unit with an injector (360HK101, 360HK301) to achieve the post dilution with potable water.

## Operation mode

Normal operation:

The sensors (360ML001-360ML004) measure the polymer level.

The sensors (360MT101-360MT401) measure the pump temperature.

The sensors (360MP101-360MP401) measure the pressure at the pump stator.

The sensors (360MF101 and 360MF501) measure the flow.

The control of dosing will be done automatically or manual.

Two possible operating modes are foreseen:

-	The polymer flow rate is calculated in proportion to the discharge flow in the outlet channel (object 200). Dosing rate is controlled to be proportional to the outlet flow measured by the flow sensor (200MF001) (Set point 360/11).

-	If requested by process conditions or during maintenance the precipitation dosing rate can be adjusted manually independently from WWTP outlet flow (Set point 360/12, Set point 360/13).

Malfunction:

In case of failure of the package unit, a fault report is set.

In case of failure of solenoid valve (360AS001, 360AS151, 360AS351), a fault report is set.

In case of a minimum level in the storage tank (360ML004) (variable set point in SCADA), a fault report is set and the dosing pumps are stopped.

In case of malfunction of a duty dosing pump, a fault report is set and the standby pump will start automatically.

In case of a maximum pressure or temperature (acc. to pump manufacturer) the dosing pumps are stopped and a fault report is set.

If a sensor is broken, a new sensor has to be installed.

## Set point values

Set point 360/11:

Specific polymer dosing in g polymer / m³ outlet flow:	i. e. 1

range 					0.1 – 1 g polymer / m³ outlet flow

-	Flow Measurement (360MF101)

-	Range:	0 - 30 m³/h

Set point 360/12:

PST 111 - 114:	Polymer solution flow rate 24.8 m³/h

-	Flow Measurement (360MF501)

-	Range:	0 - 10 m³/h

Set point 360/13:

PST 115		Polymer solution flow rate 6.2 m³/h

The set point values which are visible in SCADA are changeable by the operator.

## Control

Control panels are located in in a separate chamber adjacent to object 350.

# Air Purification Pre-Thickener (270)

## General description

To avoid smell leaks from sludge thickening, the tank is covered and air below the covered spaces is extracted and treated in a biofilter.

## Characteristics

Surface area thickener:		314 m²

Air volume:				approx. 346 m³

Air change:				5 -fold

Chosen waste air exchange:		1,800 m³/h

Filtration rate biofilter:		150 m³/m²

Required biofilter surface:		12 m²

Chosen biofilter surface:		18 m²

## Functional process description

The heart of the biofilter (270HK102) is the filter bed consisting of organic material. A natural microflora is colonising on the large surface of the chosen filter medium. Good biofilter media with a high biological activity stimulate multiplication and adaptation of micro-organisms by supplying optimal growth conditions. The pollutants are (ad)sorbed by the large inner surface of the biofilter medium and catabolised by the microorganisms within the biofilm.

To preserve the optimum conditions of growth and degradation for the microorganism waste air is convoyed by help of a ventilator (270AL101) towards an upstream scrubber unit before feeding in biofilter. This scrubber is a packed column integrated into the distribution chamber of the biofilter for conditioning of the inlet air: In the simplest application pre-conditioning relates to humidifying the waste air up to saturation. The humidification allows maintaining the water content of the biofilter medium at a sufficient level, needed for proper functioning of the microorganisms. The humidification works with potable water from the potable water booster station (object 390).

## Operation modi

Normal operation

In normal mode the extractor fan (270AL101) is in operation. The waste air will be collected and transferred via the scrubber to the biofilter (unit 270).

Malfunction

In case of malfunction of the extractor fan, a fault report is set

In case of breakdown of the extractor fan, employees who must enter closed areas below the cover with risk for gas are to be equipped with gas warning devices. The operators have to install spare air blower.

## Control

The local package unit control cabinet is mounted near to the biofilter. The overall control is located in MCB inside the new building (unit 960).

# Air Purification Aerobic Digester (370)

## General description

To avoid smell leaks from sludge digester, parts are covered and air from the covered spaces is extracted and treated in a biofilter.

## Characteristics

Aeration capacity of digester:	6,828 Nm³/h

Chosen waste air exchange:		8,000 m³/h

Filtration rate biofilter:		150 m³/m²

Required biofilter surface:		57 m²

Chosen biofilter surface:		60 m²

## Functional process description

The heart of the biofilter (370HK102) is the filter bed consisting of organic material. A natural microflora is colonising on the large surface of the chosen filter medium. Good biofilter media with a high biological activity stimulate multiplication and adaptation of micro-organisms by supplying optimal growth conditions. The pollutants are (ad)sorbed by the large inner surface of the biofilter medium and catabolised by the microorganisms within the biofilm.

To preserve the optimum conditions of growth and degradation for the microorganism waste air is convoyed by help of a ventilator (370AL101) towards an upstream scrubber unit before feeding in biofilter. This scrubber is a packed column integrated into the distribution chamber of the biofilter for conditioning of the inlet air: In the simplest application pre-conditioning relates to humidifying the waste air up to saturation. The humidification allows maintaining the water content of the biofilter medium at a sufficient level, needed for proper functioning of the microorganisms. The humidification works with potable water from the potable water booster station (object 390).

## Operation modi

Normal operation

In normal mode the extractor fan (370AL101) is in operation. The waste air will be collected and transferred via the scrubber to the biofilter (unit 370).

Malfunction

I In case of malfunction of the extractor fan, a fault report is set

In case of breakdown of the extractor fan, employees who must enter closed areas below the cover with risk for gas are to be equipped with gas warning devices. The operators have to install spare air blower.

## Control

The local package unit control cabinet is mounted near to the biofilter. The overall control located in MCB above the pumping station (unit 120).

# Process water booster station (390)

## General description

The potable water booster station (object 390) serves all facility parts with potable water. The booster station will be dry installed inside the chemical dosing building (object 350).

## Characteristics

Dry installed pumps:		2 + 1

Capacity booster station:	2 x 30 m³/h

Pressure head:			40 m

## Functional process description

The potable water booster station (object 390) consist of three potable water pumps (390AP001/002/003) feed by an existent potable water network. The pumps convey the water to the coarse and fine screen buildings (object 060 and 065), the primary sludge pumping station (object 120), the aerobic digester (object 310), the digested sludge pumping station (object 315), the emergency combined eye shower and shower (350MH001), the precipitation station (object 350), the air purification pre-thickener (object 270), the air purification (object 370), the control room (object 500) and hydrants.

The potable water pumps possess an overpressure switch (390MP002) as protection device. The pipes are fitted with all necessary valves. The potable water flow is measured and recorded (120MF101). The pumps are controlled by pressure measurement (390MP001).

A pump sump for pump leakage with a level measurement (390ML102) is existing inside the chemical dosing building (object 350).

## Operation modi

Normal operation

The pumping station is operated automatically. One pump (390AP001/002/003) will be working. If the water demand is bigger than the capacity of the first duty pump and the pressure in the network decreases below pre-selected 4 bar the second pump will start automatically. The pumps are operated in an alternating sequence in order to minimise the wear of the pumps. The operational status of the pumps is monitored by the SCADA system

Malfunction

In case of malfunction of a pump, a fault report is set. The stand-by pump will start automatically.

In case of booster station failure an alarm occurs and the local Package Unit Control Cabinet gives a signal to the Scada system.

In case of leakage detected by level measurement (390ML102) an alarm is set.

## Set point values

-	Pressure measurement (390MP001)

-	Range: 	0 – 6 bar

Set point 390/11: A pressure sensor (390MP001) controls the number of the working pumps

4.0 bar

Set point 390/12:	operation time of an aggregate to change

duty and standby:			24 h

The set point values which are visible in Scada are changeable by the operator.

## Control

The local package unit control cabinet is mounted near to the pump skid. The overall control is located in MCB adjacent to the chemical dosing building (object 350).

# Wastewater Pumping Station (300)

## General description

Two submersible pumps (1 duty +1 stand-by) are designed in order to displace the wastewater from control room (object 500) as well as condensate from the biofilters (object 270 and 370) and drainage of the screenings and grit containers (object 060 and 065) towards the inlet chamber of the coarse screen building (unit 060).

## Characteristics

Wet installed pumps:		1 + 1

Capacity:				54 m³/h, each

Pressure head:			8 m

## Functional process description

The wastewater drainage pumps (300AP101/201) are controlled by an ultrasonic level measurement (300ML101) inside the wet chamber. If the water level is higher than a pre-selected level approx. 294.45 m (set point 300/11) one pump starts operation. If the level is below a pre selected level approx. 294.20 m (set point 300/12) the pump stops operation. A new start is possible after passing 10 minutes time period (set point 300/14) and with a level higher than necessary cover level above the pumps. The maximal permissible level inside the sump is 295.45 m (set point 300/13).

The cycling between the pumps will be done when a pre selected operation time (set value 300/15) has elapsed.

## Operation modi

Normal operation

The pumping station is operated automatically. One pump (300AP101 / 201) will be working.

Malfunction

In case of malfunction of the duty pump, a fault report is set and the stand-by pump starts running.

If a sensor is broken, a new sensor has to be installed.

## Set point values

-	Level measurement (300ML101)

Range: 0 - 5 m

Set point 300/11:		Water level inside the pumping station, which starts operating pump (300AP101 / 201):				+ 0.45 m

Set point 300/12:		Water level inside the pumping station, which stops operation pump (300AP101 / 201):				+ 0.25 m

Set value 300/13:	Max. water level inside the pumping station 	+ 1.45 m

Set value 300/14:	Predefined time sequence for a restart of duty pump	10 minutes

Set point 300/15:		Operation time of a pump to change duty and stand-by

The set point values which are visible in SCADA are changeable by the operator.

## Control

Control panels are located in in a separate chamber adjacent to object 350.