## Summary
ხარჯთაღრიცხვის ღირებულება
| Material | Salary | Sum | Profit | Additional expenses | Startup and as built | V.A.T | Final
Heating & Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water & Sewege | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Total | 0

## H&C
| Description | U/M | Quantity | Price | Sum of Material cost | Install. | Sum of Install. Cost | Sum
1 | 4-way blow Cassette type FCU, 4 pipe system - (Cooling 5,5KW) | pcs | 2 |  | 0 |  | 0 | 0
2 | 4-way blow Cassette type FCU, 2 pipe system - (Cooling 4,5KW) | pcs | 24 |  | 0 |  | 0 | 0
3 | 4-way blow Cassette type FCU, 4 pipe system - (Cooling 4,5KW) | pcs | 42 |  | 0 |  | 0 | 0
4 | FCU Controller, for two fancoils each | pcs | 70 |  | 0 |  | 0 | 0
5 | Signal Cable for FCU Controller | pcs | 1050 |  | 0 |  | 0 | 0
6 | Brass Y-Strainer Dn15 | pcs | 133 |  | 0 |  | 0 | 0
7 | Brass Y-Strainer Dn20 | pcs | 160 |  | 0 |  | 0 | 0
8 | Brass Ball Valve Dn20 | pcs | 648 |  | 0 |  | 0 | 0
9 | Brass Ball Valve Dn15 | pcs | 1120 |  | 0 |  | 0 | 0
10 | 2-way Pressure independent Balancing and Control Valve with modulating actuator Dn15 | pcs | 133 |  | 0 |  | 0 | 0
11 | 2-way Pressure independent Balancing and Control Valve with modulating actuator Dn20 | pcs | 157 |  | 0 |  | 0 | 0
12 | Air Vent | pcs | 307 |  | 0 |  | 0 | 0
13 | PP Pipe, Drainage for condensate, ⌀50 | m | 720 |  | 0 |  | 0 | 0
14 | PP Pipe, Drainage for condensate, ⌀32 | m | 630 |  | 0 |  | 0 | 0
15 | Cast Iron Ball Valve Dn80 | pcs | 18 |  | 0 |  | 0 | 0
16 | Differencial Pressure Control Valve Dn80 | pcs | 6 |  | 0 |  | 0 | 0
17 | Rubber insulation 48/9mm | m | 720 |  | 0 |  | 0 | 0
18 | Rubber insulation 35/9mm | m | 630 |  | 0 |  | 0 | 0
19 | Galvanised Steel Pipe Dn80 | m | 382 |  | 0 |  | 0 | 0
20 | Galvanised Steel Pipe Dn65 | m | 377 |  | 0 |  | 0 | 0
21 | Galvanised Steel Pipe Dn50 | m | 267 |  | 0 |  | 0 | 0
22 | Galvanised Steel Pipe Dn40 | m | 233 |  | 0 |  | 0 | 0
23 | Galvanised Steel Pipe Dn32 | m | 275 |  | 0 |  | 0 | 0
24 | Galvanised Steel Pipe Dn25 | m | 805 |  | 0 |  | 0 | 0
25 | Galvanised Steel Pipe Dn20 | m | 1775 |  | 0 |  | 0 | 0
26 | Galvanised Steel Pipe Dn15 | m | 1250 |  | 0 |  | 0 | 0
27 | Galvanised steel pipe hanging materials | set | 35% |  | 0 |  | 0 | 0
| Galvanised steel pipe fittings |  | 50% |  | 0 |  | 0 | 0
28 | Rubber insulation 89/19mm | m | 362 |  | 0 |  | 0 | 0
29 | Rubber insulation 77/19mm | m | 357 |  | 0 |  | 0 | 0
30 | Rubber insulation 63/19mm | m | 237 |  | 0 |  | 0 | 0
31 | Rubber insulation 48/19mm | m | 227 |  | 0 |  | 0 | 0
32 | Rubber insulation 42/19mm | m | 705 |  | 0 |  | 0 | 0
33 | Rubber insulation 35/19mm | m | 2955 |  | 0 |  | 0 | 0
34 | Rubber insulation 28/19mm | m | 2695 |  | 0 |  | 0 | 0
35 | Rubber insulation 22/19mm | m | 1250 |  | 0 |  | 0 | 0
36 | Brass Ball Valve Dn32 | pcs | 22 |  | 0 |  | 0 | 0
37 | Brass Ball Valve Dn40 | pcs | 9 |  | 0 |  | 0 | 0
38 | Balancing Valve Dn40 | pcs | 2 |  | 0 |  | 0 | 0
39 | Panel Radiator 1500X800 (with thermostatic valve set) | pcs | 68 |  | 0 |  | 0 | 0
40 | Heating Manifold 1' for Radiators (6+6 3/4' nipples, flow meters on the supply bars, thermostatic valves on the return bars, manual air vent valve/swivel drain valve, 2 pc.s) | pcs | 2 |  | 0 |  | 0 | 0
41 | Hot water Pipe PP-R ⌀40 | m | 440 |  | 0 |  | 0 | 0
42 | Hot water Pipe PP-R ⌀32 | m | 2120 |  | 0 |  | 0 | 0
43 | Hot water Pipe PP-R ⌀25 | m | 900 |  | 0 |  | 0 | 0
44 | Steel Pipe Fittings |  | 50% |  | 0 |  | 0 | 0
45 | PP Pipe Fittings | set |  |  | 0 |  | 0 | 0
46 | PP-R Pipe Fittings | set | 35% |  | 0 |  | 0 | 0
47 | Pipe Hangers and Fasteners | set | 20% |  | 0 |  | 0 | 0
48 | Brass Ball Valve Dn25 | pcs | 36 |  | 0 |  | 0 | 0
49 | Balancing Valve Dn32 | pcs | 6 |  | 0 |  | 0 | 0
50 | Chiller, MAXA 257 kW, model 04258, scroll compressor, with hydronic module, 2x pump VFD (PICV SYSTEM) | pcs | 2 |  | 0 |  | 0 | 0
51 | Medium Pressure Duct type FCU, 4 pipe system - (Cooling 4,5KW) | pcs | 88 |  | 0 |  | 0 | 0
52 | Cast Iron Y-Strainer Flanged Dn125 | pcs | 2 |  | 0 |  | 0 | 0
53 | Vibration Absorber Dn125 | pcs | 4 |  | 0 |  | 0 | 0
54 | Cast Iron Gate Valve flanged Dn125 | pcs | 6 |  | 0 |  | 0 | 0
55 | Cast Iron Gate Valve flanged Dn200 | pcs | 2 |  | 0 |  | 0 | 0
56 | Flow Switch | pcs | 3 |  | 0 |  | 0 | 0
57 | Safety group | pcs | 6 |  | 0 |  | 0 | 0
58 | Brass Check Valve Dn25 | pcs | 3 |  | 0 |  | 0 | 0
59 | Brass Y-Strainer Dn25 | pcs | 3 |  | 0 |  | 0 | 0
60 | Thermomanometer | pcs | 26 |  | 0 |  | 0 | 0
61 | Galvanised Steel Pipe Dn200 | m | 20 |  | 0 |  | 0 | 0
62 | Galvanised Steel Pipe Dn150 | m | 14 |  | 0 |  | 0 | 0
63 | Galvanised Steel Pipe Dn125 | m | 22 |  | 0 |  | 0 | 0
64 | Galvanised Steel Pipe Dn100 | m | 42 |  | 0 |  | 0 | 0
65 | Galvinised steel pipe fittings | set | 50% |  | 0 |  | 0 | 0
66 | Galvanised steel pipe hanging and fastening |  | 35% |  | 0 |  | 0 | 0
67 | Rubber insulation 225/19mm + Moisture barrier rockwool roll + protective jacket sheet metal | m | 20 |  | 0 |  | 0 | 0
68 | Rubber insulation 142/19mm + Moisture barrier rockwool roll + protective jacket sheet metal | m | 15 |  | 0 |  | 0 | 0
69 | Rubber insulation 163/19mm | m | 14 |  | 0 |  | 0 | 0
70 | Rubber insulation 114/19mm | m | 27 |  | 0 |  | 0 | 0
71 | Condensing Gas Boiler - 290 KW (80°-60°) | pcs | 2 |  | 0 |  | 0 | 0
72 | Plate Heat Exchanger - 290 KW (80°-60°) | pcs | 2 |  | 0 |  | 0 | 0
73 | Inline type pump, VFD control and automation; L=12.5 m3/h; H= 8 m | pcs | 2 |  | 0 |  | 0 | 0
74 | Circulation Pump, VFD L=7,81 m3/h ; H=13m | pcs | 1 |  | 0 |  | 0 | 0
75 | Circulation Pump, VFD L=6,56 m3/h ; H=13m | pcs | 1 |  | 0 |  | 0 | 0
76 | Circulation Pump, VFD L=5,94 m3/h ; H=13m | pcs | 1 |  | 0 |  | 0 | 0
77 | Circulation Pump, VFD L=3,87 m3/h ; H=12m | pcs | 1 |  | 0 |  | 0 | 0
78 | Volume Tank 200L | pcs | 3 |  | 0 |  | 0 | 0
79 | Cast Iron Y-Strainer Flanged Dn100 | pcs | 4 |  | 0 |  | 0 | 0
80 | Cast Iron Gate Valve flanged Dn100 | pcs | 16 |  | 0 |  | 0 | 0
81 | Cast Iron Gate Valve flanged Dn80 | pcs | 13 |  | 0 |  | 0 | 0
82 | Cast Iron Gate Valve flanged Dn65 | pcs | 9 |  | 0 |  | 0 | 0
83 | Cast Iron Check Valve flanged Dn100 | pcs | 3 |  | 0 |  | 0 | 0
84 | Vibration Absorber Dn100 | pcs | 8 |  | 0 |  | 0 | 0
85 | Vibration Absorber Dn80 | pcs | 12 |  | 0 |  | 0 | 0
86 | Vibration Absorber Dn65 | pcs | 2 |  | 0 |  | 0 | 0
87 | Vibration Absorber Dn50 | pcs | 4 |  | 0 |  | 0 | 0
88 | Vibration Absorber Dn40 | pcs | 2 |  | 0 |  | 0 | 0
89 | Heating manifold - Dn200; L=1500mm | pcs | 2 |  | 0 |  | 0 | 0
90 | Brass Ball Valve Dn50 | pcs | 9 |  | 0 |  | 0 | 0
91 | Brass Check Valve Dn20 | pcs | 3 |  | 0 |  | 0 | 0
92 | Cast Iron Y-Strainer Flanged Dn65 | pcs | 3 |  | 0 |  | 0 | 0
93 | Brass Y-Strainer Dn50 | pcs | 3 |  | 0 |  | 0 | 0
94 | Brass Y-Strainer Dn40 | pcs | 2 |  | 0 |  | 0 | 0
95 | Boiler Exhaust Pipe, Stainless Steel, Dn 350, With Anticondensation and Fireproof Insulation, Protective Layer of Galvanized Steel | m | 35 |  | 0 |  | 0 | 0
96 | Convector - Trench Heater with fan (243mm x 125mm; L=3000) with thermostatic and air valves | pcs | 72 |  | 0 |  | 0 | 0
97 | Heating Manifold 1' for Radiators (4+4 3/4' nipples, flow meters on the supply bars, thermostatic valves on the return bars, manual air vent valve/swivel drain valve, 2 pc.s) | pcs | 4 |  | 0 |  | 0 | 0
98 | Cold water Pipe PP-R ⌀32 | m | 20 |  | 0 |  | 0 | 0
99 | Cold water Pipe PP-R ⌀25 | m | 20 |  | 0 |  | 0 | 0
100 | PPR pipe fittings | set | 35% |  | 0 |  | 0 | 0
101 | PPR pipe Hanging and fastening |  | 20% |  | 0 |  | 0 | 0
102 | Rubber insulation 142/19mm | m | 7 |  | 0 |  | 0 | 0
103 | Cast Iron Ball Valve Dn65 | pcs | 6 |  | 0 |  | 0 | 0
104 | Differencial Pressure Control Valve Dn65 | pcs | 2 |  | 0 |  | 0 | 0
105 | Balancing Valve Dn25 | pcs | 1 |  | 0 |  | 0 | 0
106 | Convector - Trench Heater with fan (243mm x 125mm; L=2000) with thermostatic and air valves | pcs | 3 |  | 0 |  | 0 | 0
107 | Heating Manifold 1' for Radiators (3+3 3/4' nipples, flow meters on the supply bars, thermostatic valves on the return bars, manual air vent valve/swivel drain valve, 2 pc.s) | pcs | 2 |  | 0 |  | 0 | 0
108 | Medium Pressure Duct type FCU, 4 pipe system - (Cooling 5,5KW) | pcs | 1 |  | 0 |  | 0 | 0
109 | Balanacing Valve Dn25 | pcs | 1 |  | 0 |  | 0 | 0
110 | Chiller, Midea 185KW, model MGB-F200W/RN1, scroll compressor | pcs | 1 |  | 0 |  | 0 | 0
111 | Hydronic module with 2 pumps (main + reserve) VFD, inline, with vfd control; with automatic; 32m3/h - 11m | pcs | 1 |  | 0 |  | 0 | 0
112 | Accumulation Tank with 5x electric heater 10kw - 750Liter | pcs | 1 |  | 0 |  | 0 | 0
113 | Pressure Gauge | pcs | 7 |  | 0 |  | 0 | 0
114 | Balancing Valve Dn65 | pcs | 2 |  | 0 |  | 0 | 0
115 | 3-Way Valve with electic actuator Dn65 | pcs | 2 |  | 0 |  | 0 | 0
116 | Balancing Valve Dn50 | pcs | 1 |  | 0 |  | 0 | 0
117 | 3-Way Valve with electic actuator Dn50 | pcs | 1 |  | 0 |  | 0 | 0
118 | 3-Way Valve with electic actuator Dn40 | pcs | 1 |  | 0 |  | 0 | 0
119 | Brass Y-Strainer Dn32 | pcs | 1 |  | 0 |  | 0 | 0
120 | 3-Way Valve with electic actuator Dn32 | pcs | 1 |  | 0 |  | 0 | 0
121 | Rubber insulation 114/19mm + Moisture barrier rockwool roll + protective jacket sheet metal | m | 15 |  | 0 |  | 0 | 0
122 | Rubber insulation 89/19mm + Moisture barrier rockwool roll + protective jacket sheet metal | m | 20 |  | 0 |  | 0 | 0
123 | Rubber insulation 77/19mm + Moisture barrier rockwool roll + protective jacket sheet metal | m | 20 |  | 0 |  | 0 | 0
124 | Rubber insulation 63/19mm + Moisture barrier rockwool roll + protective jacket sheet metal | m | 30 |  | 0 |  | 0 | 0
125 | Rubber insulation 48/19mm + Moisture barrier rockwool roll + protective jacket sheet metal | m | 10 |  | 0 |  | 0 | 0
126 | Rubber insulation 42/19mm + Moisture barrier rockwool roll + protective jacket sheet metal | m | 10 |  | 0 |  | 0 | 0
127 | COMPUTER ROOM AIR CONDITIONING UNIT (CRAC), DX SYSTEM with connection copper pipes, damper(s), safety detectors, sensors and automation included, Cooling Capacity 30 kW: 1) Indoor Unit 2) Outdoor Unit (Condenser) | pcs | 2 |  | 0 |  | 0 | 0
128 | Cold water Pipe PP-R ⌀50, D50 Heating and Cooling system risers drain | m | 60 |  | 0 |  | 0 | 0
129 | Ball Valve, Dn32 (Drain riser) | pcs | 48 |  | 0 |  | 0 | 0
130 | Steel for equipment platform (square, corner, welding materials) | set | 8 |  | 0 |  | 0 | 0
[5 empty] | 0 |  | 0 | 0
| Profit |  |  | 10% |  |  |  | 0
0
| Overhead Cost |  |  | 5% |  |  |  | 0
0
| Startup, comissioning & as build drawings |  |  | 3% |  |  |  | 0
0
| V.A.T |  |  | 18% |  |  |  | 0
| Sum | [6 empty] | 0

## Lisi Ventilation
| Description | U/M | Quantity | Price | Sum of Material cost | Install. | Sum of Install. Cost | Sum
1 | Ducts from galvanised steel 0,5mm | m2 | 640 |  | 0 |  | 0 | 0
2 | Ducts from galvanised steel 1mm | m2 | 730 |  | 0 |  | 0 | 0
3 | Ducts from galvanised steel 0,7mm | m2 | 1640 |  | 0 |  | 0 | 0
| Duct Hanging Materials | bundle | 25% |  | 0 |  |  | 0
4 | Duct insulation, self-adhesive rubber foam 13mm | m2 | 3010 |  | 0 |  | 0 | 0
5 | Insulated Plenum Box, with Louvre-faced Ceiling Diffuser (Kesklima CDA Prototype) 450*450 (300*300) | pcs | 314 |  | 0 |  | 0 | 0
6 | Round Diffuser ⌀125 | pcs | 56 |  | 0 |  | 0 | 0
7 | Motorised Fire Damper 24V (normally open) 950X350 | pcs | 2 |  | 0 |  | 0 | 0
8 | Motorised Fire Damper 24V (normally open) 850X350 | pcs | 2 |  | 0 |  | 0 | 0
9 | Motorised Fire Damper 24V (normally open) 700X300 | pcs | 1 |  | 0 |  | 0 | 0
10 | Motorised Fire Damper 24V (normally open) 200X200 | pcs | 7 |  | 0 |  | 0 | 0
11 | Mechanical Damper ⌀150 | pcs | 280 |  | 0 |  | 0 | 0
12 | Mechanical Damper ⌀200 | pcs | 24 |  | 0 |  | 0 | 0
13 | Mechanical Damper 200X200 | pcs | 14 |  | 0 |  | 0 | 0
14 | Mechanical Damper 250X200 | pcs | 17 |  | 0 |  | 0 | 0
15 | Mechanical Damper 250X250 | pcs | 2 |  | 0 |  | 0 | 0
16 | Mechanical Damper 300X200 | pcs | 15 |  | 0 |  | 0 | 0
17 | Mechanical Damper 400X200 | pcs | 3 |  | 0 |  | 0 | 0
18 | Mechanical Damper 450X200 | pcs | 2 |  | 0 |  | 0 | 0
19 | Mechanical Damper 700X300 | pcs | 4 |  | 0 |  | 0 | 0
20 | Linear 4 Slot Diffuser, L=1m, with Plenum Box, For Ducted Fancoils | pcs | 88 |  | 0 |  | 0 | 0
21 | Motorised Fire Damper 24V (normally open) 800X500 | pcs | 1 |  | 0 |  | 0 | 0
22 | Motorised Fire Damper 24V (normally open) 550X450 | pcs | 1 |  | 0 |  | 0 | 0
23 | Motorised Fire Damper 24V (normally open) 500X250 | pcs | 2 |  | 0 |  | 0 | 0
24 | Motorised Fire Damper 24V (normally open) 250X150 | pcs | 1 |  | 0 |  | 0 | 0
25 | Mechanical Damper 800X300 | pcs | 1 |  | 0 |  | 0 | 0
26 | Motorised Fire Damper 24V (normally open) 750X300 | pcs | 3 |  | 0 |  | 0 | 0
27 | Motorised Fire Damper 24V (normally open) 600X300 | pcs | 3 |  | 0 |  |  | 0
28 | Mechanical Damper 500X200 | pcs | 3 |  | 0 |  | 0 | 0
29 | Mechanical Damper 600X200 | pcs | 7 |  | 0 |  | 0 | 0
30 | Mechanical Damper 350X200 | pcs | 1 |  | 0 |  | 0 | 0
31 | Round Diffuser ⌀250 | pcs | 13 |  | 0 |  | 0 | 0
32 | Linear 4 Slot Diffuser, L=2m, with Plenum Box, For Ducted Fancoils | pcs | 1 |  | 0 |  | 0 | 0
33 | Motorised Fire Damper 24V (normally open) 400X200 | pcs | 1 |  | 0 |  | 0 | 0
34 | Motorised Fire Damper 24V (normally open) 250X200 | pcs | 1 |  | 0 |  | 0 | 0
35 | Toilet Exhaust Fan (box type) - 4660m3/h -350pa | pcs | 1 |  | 0 |  | 0 | 0
36 | Wire mesh grill 1300X600 | pcs | 12 |  | 0 |  | 0 | 0
37 | Motorised Fire Damper 24V (normally open) 650X250 | pcs | 1 |  | 0 |  | 0 | 0
38 | Protective layer from Galvanized sheet metal, 0.5mm | pcs | 230 |  | 0 |  | 0 | 0
40 | SE-2. Supply: 10500 m3h 500 pa: Panel Filter F7, Rotary exchanger, Plug Fan VFD, 2 pipe water radiator, Silencer. Exhaust: 8700 500pa m3h 350 pa: Silencer, Panel Filter M5, Plug Fan VFD, Rotary exchanger. Heating intake air 11.3 degrees/achieve air 22C Capacity 37.8kW, Cooling intake air 30.8C/achieve air 22 °C / 60 % Capacity: Sensible/Total 30kW/54.5kW. Rotary exchanger temperatures: Supply winter -8C/11.3C, Supply summer 38C/30C, Exhaust winter 20C/-1.7C, Summer Exhaust 27C/36.4C. Equipped with sensors and auto-operation system VVS100c-R-FRVCS/VVS100c-L-SFVR_cd | pc. | 1 |  | 0 |  | 0 | 0
41 | SE-1. Supply: 10000 m3h 500 pa: Panel Filter F7, Rotary exchanger, Plug Fan VFD, 2 pipe water radiator, Silencer. Exhaust: 8800 500pa m3h 350 pa: Silencer, Panel Filter M5, Plug Fan VFD, Rotary exchanger. Heating intake air 11.3 degrees/achieve air 22C Capacity 37.8kW, Cooling intake air 30.8C/achieve air 22 °C / 60 % Capacity: Sensible/Total 30kW/54.5kW. Rotary exchanger temperatures: Supply winter -8C/11.3C, Supply summer 38C/30C, Exhaust winter 20C/-1.7C, Summer Exhaust 27C/36.4C. Equipped with sensors and auto-operation system VVS100c-R-FRVCS/VVS100c-L-SFVR_cd | pc. | 1 |  | 0 |  | 0 | 0
42 | SE-3. Supply: 6600 m3h 500 pa: Panel Filter F7, Rotary exchanger, Plug Fan VFD, 2 pipe water radiator, Silencer. Exhaust: 4500 450pa m3h 350 pa: Silencer, Panel Filter M5, Plug Fan VFD, Rotary exchanger. Heating intake air 9 degrees/achieve air 22C Capacity 29kW, Cooling intake air 30.8C/achieve air 22 °C / 60 % Capacity: Sensible/Total 21kW/38.7kW. Rotary exchanger temperatures: Supply winter -8C/9C, Supply summer 38C/31.2C, Exhaust winter 20C/-3.2C, Summer Exhaust 27C/36.9C. Equipped with sensors and auto-operation system VVS055c-R-FRVCS/VVS055c-L-SFVR_cd | pc. | 1 |  | 0 |  | 0 | 0
43 | SE-4. Supply: 3240 m3h 300 pa: Panel Filter F7, Rotary exchanger, Plug Fan VFD, 2 pipe water radiator, Silencer. Exhaust: 1280 m3h 300 pa: Silencer, Panel Filter M5, Plug Fan VFD, Rotary exchanger. Heating intake air 4.1 degrees/achieve air 22C Capacity 19.5kW, Cooling intake air 33.2°C/achieve air 22 °C / 60 % Capacity: Sensible/Total 12.5/21.2 kW. Rotary exchanger temperatures: Supply winter -8C/4.1C, Supply summer 38C/33.2C, Exhaust winter 20C/-5C, Summer Exhaust 27C/37.5C. Equipped with sensors and auto-operation system VVS030c-R-FRVCS/VVS030c-L-SFVR_cd | pc. | 1 |  | 0 |  | 0 | 0
44 | SE-5. Supply: 2500 m3h 300 pa: Panel Filter F7, Rotary exchanger, Plug Fan VFD, 2 pipe water radiator, Silencer. Exhaust: 1900 m3h 300 pa: Silencer, Panel Filter M5, Plug Fan VFD, Rotary exchanger. Heating intake air 10.1 degrees/achieve air 22C Capacity 10kW, Cooling intake air 30.8C/achieve air 22 °C / 60 % Capacity: Sensible/Total 7.6/13.7 kW. Rotary exchanger temperatures: Supply winter -8C/10.1C, Supply summer 38C/30C, Exhaust winter 20C/-2.3C, Summer Exhaust 27C/36.4C. Equipped with sensors and auto-operation system VVS021c-R-FRVCS/VVS021c-L-SFVR_cd | pc. | 1 |  | 0 |  | 0 | 0
45 | Kitchen Exhaust Fan - 6000m3/h - 500pa | pc. | 1 |  | 0 |  | 0 | 0
46 | Belimo Actuators | pc | 26 |  | 0 |  | 0 | 0
[5 empty] | 0 |  | 0 | 0
| Profit |  |  | 10% |  |  |  | 0
0
| Overhead Cost |  |  | 5% |  |  |  | 0
0
| Startup, comissioning & as build drawings |  |  | 3% |  |  |  | 0
0
| V.A.T |  |  | 18% |  |  |  | 0
| Sum | [6 empty] | 0

## Water&Sewege
| Description | U/M | Quantity | Price | Sum of Material cost | Install. | Sum of Install. Cost | Sum
1 | PP-R Pipe, for Cold Water, ⌀75 SDR6 | m | 30 |  | 0 |  | 0 | 0
2 | PP-R Pipe, for Hot Water, ⌀63 SDR6 | m | 50 |  | 0 |  | 0 | 0
3 | PP-R Pipe, for Hot Water, ⌀40 SDR6 | m | 50 |  | 0 |  | 0 | 0
4 | Rubber Insulation 77/13mm | m | 30 |  | 0 |  | 0 | 0
5 | Rubber Insulation 65/13mm | m | 50 |  | 0 |  | 0 | 0
6 | Rubber Insulation 42/13mm | m | 75 |  | 0 |  | 0 | 0
7 | PP Pipe, Sewage, ⌀160 | m | 80 |  | 0 |  | 0 | 0
8 | PP Pipe Fittings | bundle | 11 |  | 0 |  | 0 | 0
9 | PP-R Pipe Fittings | bundle | 11 |  | 0 |  | 0 | 0
10 | Pipe Hangers and Fasteners | bundle | 11 |  | 0 |  | 0 | 0
11 | Modular Water Reservoir, Galvanized Steel (For Potable Water), 8 m3 - exact dimensions to be confirmed | pcs | 1 |  | 0 |  | 0 | 0
12 | Brass Ball Valve Dn25 | pcs | 23 |  | 0 |  | 0 | 0
13 | Brass Ball Valve Dn20 | pcs | 22 |  | 0 |  | 0 | 0
14 | Single-jet dry dial water m (antimagnetic) for cold water Dn 25 | pcs | 8 |  | 0 |  | 0 | 0
15 | PP-R Pipe, for Cold Water, ⌀32 SDR6 | m | 110 |  | 0 |  | 0 | 0
16 | PP-R Pipe, for Cold Water, ⌀25 SDR6 | m | 350 |  | 0 |  | 0 | 0
17 | Rubber Insulation 35/13mm | m | 120 |  | 0 |  | 0 | 0
18 | Rubber Insulation 28/13mm | m | 545 |  | 0 |  | 0 | 0
19 | PP Pipe, Sewage, ⌀200 | m | 25 |  | 0 |  | 0 | 0
20 | PP Pipe, Sewage, ⌀110 | m | 225 |  | 0 |  | 0 | 0
21 | PP Pipe, Sewage, ⌀50 | m | 200 |  | 0 |  | 0 | 0
22 | Hot water boiler, with single serpentine heat-exchanger, V=1000L | pcs | 3 |  | 0 |  | 0 | 0
23 | Variable speed unit: Pressure booster with three three-phase vertical pumps (2 working 50% duty, 1 stand-by), with hydraulics in AISI 304 or AISI 316 and, with integrated E-SPD inverter. 3,2 m3/h; 8bar | pcs | 1 |  | 0 |  | 0 | 0
24 | Circulation Pump, Invertor L=2.5m3/h ; H=6m | pcs | 3 |  | 0 |  | 0 | 0
25 | Water Level Ultrasonic Sensor, level probe | pcs | 1 |  | 0 |  | 0 | 0
26 | Motorized Ball Valve Dn50 - Stainless Steel Electrical Ball Valve with Full Port, 9-24V | pcs | 1 |  | 0 |  | 0 | 0
27 | Vibration Absorber Dn50 | pcs | 2 |  | 0 |  | 0 | 0
28 | Brass Ball Valve Dn50 | pcs | 10 |  | 0 |  | 0 | 0
29 | Brass Ball Valve Dn32 | pcs | 6 |  | 0 |  | 0 | 0
30 | Brass Ball Valve Dn15 | pcs | 19 |  | 0 |  | 0 | 0
31 | Brass Y-Strainer Dn50 | pcs | 2 |  | 0 |  | 0 | 0
32 | Brass Y-Strainer Dn32 | pcs | 2 |  | 0 |  | 0 | 0
33 | Brass Check Valve Dn50 | pcs | 1 |  | 0 |  | 0 | 0
34 | Brass Check Valve Dn32 | pcs | 1 |  | 0 |  | 0 | 0
35 | Brass Check Valve Dn25 | pcs | 3 |  | 0 |  | 0 | 0
36 | Volume Tank 50L | pcs | 3 |  | 0 |  | 0 | 0
37 | Safety Group | pcs | 6 |  | 0 |  | 0 | 0
38 | Water Pressure Reducing Valve Dn32 | pcs | 1 |  | 0 |  | 0 | 0
39 | Single-jet dry dial water m (antimagnetic) for cold water Dn 32 | pcs | 1 |  | 0 |  | 0 | 0
40 | PP-R Pipe, for Cold Water, ⌀40 SDR6 | m | 25 |  | 0 |  | 0 | 0
41 | PP-R Pipe, for Cold Water, ⌀20 SDR6 | m | 165 |  | 0 |  | 0 | 0
42 | PP-R Pipe, for Hot Water, ⌀32 SDR6 | m | 10 |  | 0 |  | 0 | 0
43 | PP-R Pipe, for Hot Water, ⌀25 SDR6 | m | 195 |  | 0 |  | 0 | 0
44 | PP-R Pipe, for Hot Water, ⌀20 SDR6 | m | 230 |  | 0 |  | 0 | 0
45 | Rubber Insulation 22/13mm | m | 395 |  | 0 |  | 0 | 0
46 | Water Pressure Reducing Valve Dn25 | m | 8 |  | 0 |  | 0 | 0
47 | Arrangement of Holes for Sewage Pipes ⌀133 | pcs | 48 |  | 0 |  | 0 | 0
48 | Arrangement of Holes for Sewage Pipes ⌀70 | pcs | 48 |  | 0 |  | 0 | 0
[5 empty] | 0 |  | 0 | 0
| Profit |  |  | 10% |  |  |  | 0
0
| Overhead Cost |  |  | 5% |  |  |  | 0
0
| Startup, comissioning & as build drawings |  |  | 3% |  |  |  | 0
0
| V.A.T |  |  | 18% |  |  |  | 0
| Sum | [6 empty] | 0