## Лист1
Technical data for AHU-1.1 |  |  |  |  | Climatic data
|  | Supply | Return | Comments |  | DB outdoor temperature | Relative humidity
Type |  | + | +
|  | Floor standed |  |  |  | С | %
Execution |  | Outdoor, for healthcare facilities |  |  | Winter time | -8 | 70
Maximum allow sizes (Length/Width/Height) | mm | according to selection |  |  | Summer time | +38 | 30
Filter 1st stage | class | G4 | G4
Filter 2nd stage | class | F7 | -
Filter3rd stage | class | F9 | -
Silencer |  | + | +
Fan |  |  |  | with frequency inverters
Airflow (according to project) | m3/hr | 6780 | 2050
ESP | Pa | 660 | 250
Heating section |  |  |  | For winter time
Transfer medium |  | Electrical | -
Tsupply air | С | 18 | -
Heat capacity | KW | according to calculations | -
Humidificator |  |  |  | For winter time
Transfer medium |  | steam | -
Relative humidity | % | not less 50% | -
Cooling section
Transfer medium |  | Water 75% + Ethyleneglycol 25% | -
Tinlet/Toutlet of water | С | 7/12 | -
Tsupply air | С | 25 | -
Cooling capacity | KW | according to calculations | -
Drops catcher |  | + | -
Side of service doors |  | Right | -
Pipes connection |  | Left | -
Control system |  | + | + | Standart package of control system, overload fans motors protection, antifreezing protection of heater, control humidity and temperature of supply air etc.
Remark |  | 1. Should be equipped by motorized dampers with actuators.
Technical data for AHU-1.2 |  |  |  |  | Climatic data
|  | Supply | Return | Comments |  | DB outdoor temperature | Relative humidity
Type |  | + | +
|  | Floor standed |  |  |  | С | %
Execution |  | Outdoor, for healthcare facilities |  |  | Winter time | -8 | 70
Maximum allow sizes (Length/Width/Height) | mm | according to selection |  |  | Summer time | +38 | 30
Filter 1st stage | class | G4 | G4
Filter 2nd stage | class | F7 | - |  | Parameters of indoor air for heatrecovery/recirculation
Filter3rd stage | class | F9 | - |  |  | DB indoor temperature | Relative humidity
Silencer |  | + | +
[6 empty] | С | %
Fan |  |  |  | with frequency inverters | Winter time | +20 | 30
Airflow (according to project) | m3/hr | 7280 | 6360 |  | Summer time | +25 | 60
ESP | Pa | 190 | 195
Heatrecovery |  |  |  | For winter time. Do not consider heat recovery for summer time.
Type |  | Plate heat recovery
Efficiency | % | not less 65%
Heating section |  |  |  | For winter time
Transfer medium |  | Electrical | -
Tsupply air | С | 22 | -
Heat capacity | KW | according to calculations | -
Cooling section
Transfer medium |  | Water 75% + Ethyleneglycol 25% | -
Tinlet/Toutlet of water | С | 7/12 | -
Tsupply air | С | 23 | -
Cooling capacity | KW | according to calculations | -
Drops catcher |  | + | -
Coil pressure drop (medium side) |  | not more 30 Kpa | -
Side of service doors |  | Left | -
Pipes connection |  | Right | -
Control system |  | + | + | Standart package of control system, overload fans motors protection, antifreezing protection of heater, control humidity and temperature of supply air etc.
Remark |  | 1. Should be equipped by motorized dampers with actuators.
Technical data for AHU-2.1 |  |  |  |  | Climatic data
|  | Supply | Return | Comments |  | DB outdoor temperature | Relative humidity
Type |  | + | +
|  | Floor standed |  |  |  | С | %
Execution |  | Outdoor, for healthcare facilities |  |  | Winter time | -8 | 70
Maximum allow sizes (Length/Width/Height) | mm | according to selection |  |  | Summer time | +38 | 30
Filter 1st stage | class | G4 | G4
Filter 2nd stage | class | F7 | - |  | Parameters of indoor air for heatrecovery/recirculation
Filter3rd stage | class | F9 | - |  |  | DB indoor temperature | Relative humidity
Silencer |  | + | +
[6 empty] | С | %
Fan |  |  |  | with frequency inverters | Winter time | +20 | 30
Airflow (according to project) | m3/hr | 1660 | 1410 |  | Summer time | +25 | 60
ESP | Pa | 740 | 260
Mixing section
Recirculated airflow | m3/hr | 1120
Heating section |  |  |  | For winter time
Transfer medium |  | Electrical | -
Tsupply air | С | 25 | -
Heat capacity | KW | according to calculations | -
Humidificator |  |  |  | For winter time
Transfer medium |  | steam | -
Relative humidity | % | not less 50% | -
Cooling section
Transfer medium |  | Water 75% + Ethyleneglycol 25% | -
Tinlet/Toutlet of water | С | 7/12 | -
Tsupply air | С | 16 | -
Cooling capacity | KW | according to calculations | -
Drops catcher |  | + | -
Coil pressure drop (medium side) |  | not more 30 Kpa | -
Side of service doors |  | Left | -
Pipes connection |  | Right | -
Control system |  | + | + | Standart package of control system, overload fans motors protection, antifreezing protection of heater, control humidity and temperature of supply air etc.
Remark |  | 1. Should be equipped by motorized dampers with actuators.
Technical data for AHU-2.2 |  |  |  |  | Climatic data
|  | Supply | Return | Comments |  | DB outdoor temperature | Relative humidity
Type |  | + | +
|  | Floor standed |  |  |  | С | %
Execution |  | Outdoor, for healthcare facilities |  |  | Winter time | -8 | 70
Maximum allow sizes (Length/Width/Height) | mm | according to selection |  |  | Summer time | +38 | 30
Filter 1st stage | class | G4 | G4
Filter 2nd stage | class | F7 | - |  | Parameters of indoor air for heatrecovery/recirculation
Filter3rd stage | class | F9 | - |  |  | DB indoor temperature | Relative humidity
Silencer |  | + | +
[6 empty] | С | %
Fan |  |  |  | with frequency inverters | Winter time | +20 | 30
Airflow (according to project) | m3/hr | 1020 | 750 |  | Summer time | +25 | 60
ESP | Pa | 240 | 200
Heatrecovery |  |  |  | For winter time. Do not consider heat recovery for summer time.
Type |  | Plate heat recovery
Efficiency | % | not less 65%
Heating section |  |  |  | For winter time
Transfer medium |  | Electrical | -
Tsupply air | С | 22 | -
Heat capacity | KW | according to calculations | -
Cooling section
Transfer medium |  | Water 75% + Ethyleneglycol 25% | -
Tinlet/Toutlet of water | С | 7/12 | -
Tsupply air | С | 23 | -
Cooling capacity | KW | according to calculations | -
Drops catcher |  | + | -
Coil pressure drop (medium side) |  | not more 30 Kpa | -
Side of service doors |  | Left | -
Pipes connection |  | Right | -
Control system |  | + | + | Standart package of control system, overload fans motors protection, antifreezing protection of heater, control humidity and temperature of supply air etc.
Remark |  | 1. Should be equipped by motorized dampers with actuators.
Technical data for AHU-3.1 |  |  |  |  | Climatic data
|  | Supply | Return | Comments |  | DB outdoor temperature | Relative humidity
Type |  | + | +
|  | Floor standed |  |  |  | С | %
Execution |  | Outdoor, for healthcare facilities |  |  | Winter time | -8 | 70
Maximum allow sizes (Length/Width/Height) | mm | according to selection |  |  | Summer time | +38 | 30
Filter 1st stage | class | G4 | G4
Filter 2nd stage | class | F7 | - |  | Parameters of indoor air for heatrecovery/recirculation
Filter3rd stage | class | F9 | - |  |  | DB indoor temperature | Relative humidity
Silencer |  | + | +
[6 empty] | С | %
Fan |  |  |  | with frequency inverters | Winter time | +20 | 30
Airflow (according to project) | m3/hr | 2780 | 2410 |  | Summer time | +25 | 60
ESP | Pa | 690 | 300
Mixing section
Recirculated airflow | m3/hr | 2130
Heating section |  |  |  | For winter time
Transfer medium |  | Electrical | -
Tsupply air | С | 25 | -
Heat capacity | KW | according to calculations | -
Humidificator |  |  |  | For winter time
Transfer medium |  | steam | -
Relative humidity | % | not less 50% | -
Cooling section
Transfer medium |  | Water 75% + Ethyleneglycol 25% | -
Tinlet/Toutlet of water | С | 7/12 | -
Tsupply air | С | 16 | -
Cooling capacity | KW | according to calculations | -
Drops catcher |  | + | -
Coil pressure drop (medium side) |  | not more 30 Kpa | -
Side of service doors |  | Left | -
Pipes connection |  | Right | -
Control system |  | + | + | Standart package of control system, overload fans motors protection, antifreezing protection of heater, control humidity and temperature of supply air etc.
Remark |  | 1. Should be equipped by motorized dampers with actuators.
Technical data for AHU-3.2 |  |  |  |  | Climatic data
|  | Supply | Return | Comments |  | DB outdoor temperature | Relative humidity
Type |  | + | +
|  | Floor standed |  |  |  | С | %
Execution |  | Outdoor, for healthcare facilities |  |  | Winter time | -8 | 70
Maximum allow sizes (Length/Width/Height) | mm | according to selection |  |  | Summer time | +38 | 30
Filter 1st stage | class | G4 | G4
Filter 2nd stage | class | F7 | - |  | Parameters of indoor air for heatrecovery/recirculation
Filter3rd stage | class | F9 | - |  |  | DB indoor temperature | Relative humidity
Silencer |  | + | +
[6 empty] | С | %
Fan |  |  |  | with frequency inverters | Winter time | +20 | 30
Airflow (according to project) | m3/hr | 1350 | 1150 |  | Summer time | +25 | 60
ESP | Pa | 740 | 220
Mixing section
Recirculated airflow | m3/hr | 1030
Heating section |  |  |  | For winter time
Transfer medium |  | Electrical | -
Tsupply air | С | 25 | -
Heat capacity | KW | according to calculations | -
Humidificator |  |  |  | For winter time
Transfer medium |  | steam | -
Relative humidity | % | not less 50% | -
Cooling section
Transfer medium |  | Water 75% + Ethyleneglycol 25% | -
Tinlet/Toutlet of water | С | 7/12 | -
Tsupply air | С | 16 | -
Cooling capacity | KW | according to calculations | -
Drops catcher |  | + | -
Coil pressure drop (medium side) |  | not more 30 Kpa | -
Side of service doors |  | Right | -
Pipes connection |  | Left | -
Control system |  | + | + | Standart package of control system, overload fans motors protection, antifreezing protection of heater, control humidity and temperature of supply air etc.
Remark |  | 1. Should be equipped by motorized dampers with actuators.
Technical data for AHU-3.3 |  |  |  |  | Climatic data
|  | Supply | Return | Comments |  | DB outdoor temperature | Relative humidity
Type |  | + | +
|  | Floor standed |  |  |  | С | %
Execution |  | Outdoor, for healthcare facilities |  |  | Winter time | -8 | 70
Maximum allow sizes (Length/Width/Height) | mm | according to selection |  |  | Summer time | +38 | 30
Filter 1st stage | class | G4 | G4
Filter 2nd stage | class | F7 | - |  | Parameters of indoor air for heatrecovery/recirculation
Filter3rd stage | class | F9 | - |  |  | DB indoor temperature | Relative humidity
Silencer |  | + | +
[6 empty] | С | %
Fan |  |  |  | with frequency inverters | Winter time | +20 | 30
Airflow (according to project) | m3/hr | 1240 | 1090 |  | Summer time | +25 | 60
ESP | Pa | 750 | 260
Mixing section
Recirculated airflow | m3/hr | 1030
Heating section |  |  |  | For winter time
Transfer medium |  | Electrical | -
Tsupply air | С | 25 | -
Heat capacity | KW | according to calculations | -
Humidificator |  |  |  | For winter time
Transfer medium |  | steam | -
Relative humidity | % | not less 50% | -
Cooling section
Transfer medium |  | Water 75% + Ethyleneglycol 25% | -
Tinlet/Toutlet of water | С | 7/12 | -
Tsupply air | С | 16 | -
Cooling capacity | KW | according to calculations | -
Drops catcher |  | + | -
Coil pressure drop (medium side) |  | not more 30 Kpa | -
Side of service doors |  | Left | -
Pipes connection |  | Right | -
Control system |  | + | + | Standart package of control system, overload fans motors protection, antifreezing protection of heater, control humidity and temperature of supply air etc.
Remark |  | 1. Should be equipped by motorized dampers with actuators.
Technical data for AHU-3.4 |  |  |  |  | Climatic data
|  | Supply | Return | Comments |  | DB outdoor temperature | Relative humidity
Type |  | + | +
|  | Floor standed |  |  |  | С | %
Execution |  | Outdoor, for healthcare facilities |  |  | Winter time | -8 | 70
Maximum allow sizes (Length/Width/Height) | mm | according to selection |  |  | Summer time | +38 | 30
Filter 1st stage | class | G4 | G4
Filter 2nd stage | class | F7 | - |  | Parameters of indoor air for heatrecovery/recirculation
Filter3rd stage | class | F9 | - |  |  | DB indoor temperature | Relative humidity
Silencer |  | + | +
[6 empty] | С | %
Fan |  |  |  | with frequency inverters | Winter time | +20 | 30
Airflow (according to project) | m3/hr | 1610 | 1390 |  | Summer time | +25 | 60
ESP | Pa | 720 | 240
Mixing section
Recirculated airflow | m3/hr | 1140
Heating section |  |  |  | For winter time
Transfer medium |  | Electrical | -
Tsupply air | С | 25 | -
Heat capacity | KW | according to calculations | -
Humidificator |  |  |  | For winter time
Transfer medium |  | steam | -
Relative humidity | % | not less 50% | -
Cooling section
Transfer medium |  | Water 75% + Ethyleneglycol 25% | -
Tinlet/Toutlet of water | С | 7/12 | -
Tsupply air | С | 16 | -
Cooling capacity | KW | according to calculations | -
Drops catcher |  | + | -
Coil pressure drop (medium side) |  | not more 30 Kpa | -
Side of service doors |  | Left | -
Pipes connection |  | Right | -
Control system |  | + | + | Standart package of control system, overload fans motors protection, antifreezing protection of heater, control humidity and temperature of supply air etc.
Remark |  | 1. Should be equipped by motorized dampers with actuators.
Technical data for AHU-3.5 |  |  |  |  | Climatic data
|  | Supply | Return | Comments |  | DB outdoor temperature | Relative humidity
Type |  | + | +
|  | Floor standed |  |  |  | С | %
Execution |  | Outdoor, for healthcare facilities |  |  | Winter time | -8 | 70
Maximum allow sizes (Length/Width/Height) | mm | according to selection |  |  | Summer time | +38 | 30
Filter 1st stage | class | G4 | G4
Filter 2nd stage | class | F7 | - |  | Parameters of indoor air for heatrecovery/recirculation
Filter3rd stage | class | F9 | - |  |  | DB indoor temperature | Relative humidity
Silencer |  | + | +
[6 empty] | С | %
Fan |  |  |  | with frequency inverters | Winter time | +20 | 30
Airflow (according to project) | m3/hr | 910 | 1170 |  | Summer time | +25 | 60
ESP | Pa | 250 | 250
Heatrecovery |  |  |  | For winter time. Do not consider heat recovery for summer time.
Type |  | Plate heat recovery
Efficiency | % | not less 65%
Heating section |  |  |  | For winter time
Transfer medium |  | Electrical | -
Tsupply air | С | 22 | -
Heat capacity | KW | according to calculations | -
Cooling section
Transfer medium |  | Water 75% + Ethyleneglycol 25% | -
Tinlet/Toutlet of water | С | 7/12 | -
Tsupply air | С | 23 | -
Cooling capacity | KW | according to calculations | -
Drops catcher |  | + | -
Coil pressure drop (medium side) |  | not more 30 Kpa | -
Side of service doors |  | Right | -
Pipes connection |  | Left | -
Control system |  | + | + | Standart package of control system, overload fans motors protection, antifreezing protection of heater, control humidity and temperature of supply air etc.
Remark |  | 1. Should be equipped by motorized dampers with actuators.
Technical data for AHU-4.1 |  |  |  |  | Climatic data
|  | Supply | Return | Comments |  | DB outdoor temperature | Relative humidity
Type |  | + | +
|  | Floor standed |  |  |  | С | %
Execution |  | Outdoor, for healthcare facilities |  |  | Winter time | -8 | 70
Maximum allow sizes (Length/Width/Height) | mm | according to selection |  |  | Summer time | +38 | 30
Filter 1st stage | class | G4 | G4
Filter 2nd stage | class | F7 | - |  | Parameters of indoor air for heatrecovery/recirculation
Filter3rd stage | class | F9 | - |  |  | DB indoor temperature | Relative humidity
Silencer |  | + | +
[6 empty] | С | %
Fan |  |  |  | with frequency inverters | Winter time | +20 | 30
Airflow (according to project) | m3/hr | 2210 | 2010 |  | Summer time | +25 | 60
ESP | Pa | 620 | 240
Mixing section
Recirculated airflow | m3/hr | 1900
Heating section |  |  |  | For winter time
Transfer medium |  | Electrical | -
Tsupply air | С | 25 | -
Heat capacity | KW | according to calculations | -
Humidificator |  |  |  | For winter time
Transfer medium |  | steam | -
Relative humidity | % | not less 50% | -
Cooling section
Transfer medium |  | Water 75% + Ethyleneglycol 25% | -
Tinlet/Toutlet of water | С | 7/12 | -
Tsupply air | С | 16 | -
Cooling capacity | KW | according to calculations | -
Drops catcher |  | + | -
Coil pressure drop (medium side) |  | not more 30 Kpa | -
Side of service doors |  | Left | -
Pipes connection |  | Right | -
Control system |  | + | + | Standart package of control system, overload fans motors protection, antifreezing protection of heater, control humidity and temperature of supply air etc.
Remark |  | 1. Should be equipped by motorized dampers with actuators.
Technical data for AHU-4.2 |  |  |  |  | Climatic data
|  | Supply | Return | Comments |  | DB outdoor temperature | Relative humidity
Type |  | + | +
|  | Floor standed |  |  |  | С | %
Execution |  | Outdoor, for healthcare facilities |  |  | Winter time | -8 | 70
Maximum allow sizes (Length/Width/Height) | mm | according to selection |  |  | Summer time | +38 | 30
Filter 1st stage | class | G4 | G4
Filter 2nd stage | class | F7 | - |  | Parameters of indoor air for heatrecovery/recirculation
Filter3rd stage | class | F9 | - |  |  | DB indoor temperature | Relative humidity
Silencer |  | + | +
[6 empty] | С | %
Fan |  |  |  | with frequency inverters | Winter time | +20 | 30
Airflow (according to project) | m3/hr | 670 | 570 |  | Summer time | +25 | 60
ESP | Pa | 180 | 190
Heatrecovery |  |  |  | For winter time. Do not consider heat recovery for summer time.
Type |  | Plate heat recovery
Efficiency | % | not less 65%
Heating section |  |  |  | For winter time
Transfer medium |  | Electrical | -
Tsupply air | С | 22 | -
Heat capacity | KW | according to calculations | -
Cooling section
Transfer medium |  | Water 75% + Ethyleneglycol 25% | -
Tinlet/Toutlet of water | С | 7/12 | -
Tsupply air | С | 23 | -
Cooling capacity | KW | according to calculations | -
Drops catcher |  | + | -
Coil pressure drop (medium side) |  | not more 30 Kpa | -
Side of service doors |  | Left | -
Pipes connection |  | Right | -
Control system |  | + | + | Standart package of control system, overload fans motors protection, antifreezing protection of heater, control humidity and temperature of supply air etc.
Remark |  | 1. Should be equipped by motorized dampers with actuators.