## Sheet1
Position | Title and technical specification | Type of document | Code of equipment | Manufacturer | Unit of measurment | Quantity | Weight, kg | Note
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Ventilation
Equipment
AHU-1.1; AHU-1.2; AHU-2.1; AHU-2.2; AHU-3.1…3.5; AHU-4.1; AHU-4.2 | Air handling units |  |  |  | pcs | 11 |  | look in mechanical schedule for more technical requirements
Fans:
EF-1.1 | Duct circular fan |  |  |  | pcs | 1
L=500 m3/hr; dP=140 Pa
TEF-1.2 | Duct circular fan |  |  |  | pcs | 1
L=270 m3/hr; dP=170 Pa
TEF-1.3 | Duct circular fan |  |  |  | pcs | 1
L=100 m3/hr; dP= 60 Pa
EF-1.4 | Duct circular fan |  |  |  | pcs | 1
L=450 m3/hr; dP= 140 Pa
EF-1.5 | Centrifugal fan or duct rectangular |  |  |  | pcs | 1
L=4040 m3/hr; dP=150 Pa
EF-1.7…1.8 | Duct circular fan |  |  |  | pcs | 2
L=1100 m3/hr; dP=80 Pa
EF-2.1 | Duct circular fan |  |  |  | pcs | 1
L=410 m3/hr; dP=120 Pa
TEF-2.2 | Duct circular fan |  |  |  | pcs | 1
L=100 m3/hr; dP=90 Pa
TEF-3.1 | Duct circular fan |  |  |  | pcs | 1
L=250 m3/hr; dP=165 Pa
EF-3.2 | Duct circular fan |  |  |  | pcs | 1
L=440 m3/hr; dP=160 Pa
TEF-4.1 | Duct circular fan |  |  |  | pcs | 1
L=100 m3/hr; dP=85 Pa
EF-4.2 | Duct circular fan |  |  |  | pcs | 1
L=160 m3/hr; dP=95 Pa
Diffusers:
Ceiling diffusers with integrated HEPA filter
CDH | 305x305x80 |  |  |  | pcs | 12 |  | ADQ-CFC Systemair or analog
| 457x457x80 |  |  |  | pcs | 16
| 557x557x80 |  |  |  | pcs | 9
| 610x610x80 |  |  |  | pcs | 7
Ceiling square diffusers:
CSD | 150x150 |  |  |  | pcs | 50 |  | DSQ Madel or analog
| 225x225 |  |  |  | pcs | 40
| 300x300 |  |  |  | pcs | 7
with insulated plenum-box for:
| 150x150 |  |  |  | pcs | 50
| 225x225 |  |  |  | pcs | 40
| 300x300 |  |  |  | pcs | 7
Rectangular grill:
RG | 300x200 |  |  |  | pcs | 3
Rectangular grill with damper:
RGD | 400x150 |  |  |  | pcs | 6
| 400x200 |  |  |  | pcs | 6
| 500x200 |  |  |  | pcs | 4
| 500x300 |  |  |  | pcs | 4
Transfer gril:
TG | 600x600 |  |  |  | pcs | 2
Anemostat
AN | DN100 |  |  |  | pcs | 7
| DN125 |  |  |  | pcs | 4
Volume dampers:
| DN100 |  |  |  | pcs | 76
| DN125 |  |  |  | pcs | 55
| DN140 |  |  |  | pcs | 11
| DN160 |  |  |  | pcs | 35
| DN180 |  |  |  | pcs | 4
| DN200 |  |  |  | pcs | 22
| DN225 |  |  |  | pcs | 19
| DN250 |  |  |  | pcs | 11
| DN280 |  |  |  | pcs | 4
| 250x200 |  |  |  | pcs | 1
| 300x200 |  |  |  | pcs | 3
| 350x200 |  |  |  | pcs | 1
| 600x300 |  |  |  | pcs | 1
Check valves:
| DN100 |  |  |  | pcs | 2
| DN125 |  |  |  | pcs | 2
| DN140 |  |  |  | pcs | 1
| DN180 |  |  |  | pcs | 3
| DN280 |  |  |  | pcs | 2
| DN500 |  |  |  | pcs | 1
| 250x150 |  |  |  | pcs | 1
| 600х300 |  |  |  | pcs | 1
| Stainless steel hood 1000x800 |  |  |  | pcs | 4
Ducts:
Supply ducts and insulation:
| Galvanised steel ductwork δ=0,7 mm |  |  |  | m2 | 563.2
| Fittings 30% |  |  |  | m2 | 168.96
| Rubber foam insulation δ = 9 mm |  |  |  | m2 | 805.376
Insulated flexible ducts:
| DN100 |  |  |  | m | 20
| DN125 |  |  |  | m | 12
| DN160 |  |  |  | m | 12
| DN200 |  |  |  | m | 16
| DN225 |  |  |  | m | 8
| DN250 |  |  |  | m | 7
Exhaust ducts:
| Galvanised steel ductwork δ=0,7 mm |  |  |  | m2 | 539
| Fittings 30% |  |  |  | m2 | 161.7
| Galvanised steel ductwork δ=0,9 mm (for DN500 duct) |  |  |  | m2 | 52
| Fittings 30% |  |  |  | m2 | 15.6
Flexible ducts:
| DN100 |  |  |  | m | 25
| DN125 |  |  |  | m | 18
| DN160 |  |  |  | m | 12
| Air System startup, commisioning and balancing |  |  |  | set | 1
Heating and cooling
Chiller #1 | Aircooled chiller Q=154 KW. T amb = +35 C. Tw in/Tw out = 12/7 C. Ethyleneglycol 25% + Water 75%. dP= not more 70 KPa. Attitude = 500 m. |  |  |  | pcs | 1
Chiller #2 | Aircooled chiller Q=90 KW. T amb = +35 C. Tw in/Tw out = 12/7 C. Ethyleneglycol 25% + Water 75%. dP= not more 70 KPa. Attitude = 500 m. |  |  |  | pcs | 1
Insulated buffer tank
| V=300 l |  |  |  | pcs | 2
| Duct cooler 800x500-3-2,0. Q=27 KW; Ta in/Ta out = 25 C/14 C; Tw in/Tw out = 7/12 C; dP= not more 20 KPa. |  |  |  | pcs | 1 |  | PGK Systemair or analog
| Pumps: | [6 empty] | with VSD
Pump1 | Circulation pump (double)
| H=16 m, V=28.5 m3/hr, Water 75% + Ethyleneglycol 25%, 12 C |  |  |  | pcs | 1 |  | 1 main, 1 standby
Pump2 | Circulation pump (double)
| H=15.6 m, V=16.1 m3/hr, Water 75% + Ethyleneglycol 25%, 12 C |  |  |  | pcs | 1 |  | 1 main, 1 standby
Strainers:
| DN20 |  |  |  | pcs | 2
| DN32 |  |  |  | pcs | 1
| DN40 |  |  |  | pcs | 6
| DN50 |  |  |  | pcs | 2
| DN65 |  |  |  | pcs | 3
| DN80 |  |  |  | pcs | 1
| DN100 |  |  |  | pcs | 1
PICV valves:
with 0-10 V motorised actuator:
| DN32 |  |  |  | pcs | 8
| DN40 |  |  |  | pcs | 1
| DN50 |  |  |  | pcs | 1
| DN65 |  |  |  | pcs | 2
Stop valves:
| DN20 |  |  |  | pcs | 4
| DN32 |  |  |  | pcs | 3
| DN40 |  |  |  | pcs | 18
| DN50 |  |  |  | pcs | 6
| DN65 |  |  |  | pcs | 10
| DN80 |  |  |  | pcs | 7
| DN100 |  |  |  | pcs | 7
Check valves:
| DN20 |  |  |  | pcs | 2
| DN80 |  |  |  | pcs | 1
| DN100 |  |  |  | pcs | 1
| Expansion tanks V=12 l |  |  |  | pcs | 2
| Termometer |  |  |  | pcs | 30
| Manometer |  |  |  | pcs | 30
| Automaic airvents |  |  |  | pcs | 20
| Dranaige valves |  |  |  | pcs | 20
| Safety valves |  |  |  | pcs | 4
PPR pipe PN16 Stabi Alu-foil
| 40x5,5 |  |  |  | m | 12
| 50x6,9 |  |  |  | m | 42
| 63x8,6 |  |  |  | m | 46
| 75x10,3 |  |  |  | m | 106
Fittings 30% of pipes cost
Tube pipe insulation Rubber foam δ=30 mm
| For De40 |  |  |  | m | 13.2
| For De50 |  |  |  | m | 46.2
| For De63 |  |  |  | m | 50.6
| For De75 |  |  |  | m | 116.6
Steel pipe GOST 10704-91
| 76x3,5 |  |  |  | m | 36
| 89x3,5 |  |  |  | m | 30
| 108x4 |  |  |  | m | 20
Fittings 30% of pipes cost
| Ethyleneglycol |  |  |  | Set | 1
VRF systems (with thermostats/control system in the kit):
Outdoor units:
| Mini VRF outdoor unit (12.1 KW cooling / 8.4 KW heating ) |  |  |  | pcs | 2 |  | RXYSCQ4TV1
| Mini VRF outdoor unit (10.2 cooling / 8.2 heating ) |  |  |  | pcs | 1 |  | RXYSQ12TY1
Indoor units:
| Casette indoor unit (2.2 cooling / 2.5 heating ) |  |  |  | pcs | 8 |  | FXFQ20B
| Casette indoor unit (2.8 cooling / 3.2 heating ) |  |  |  | pcs | 1 |  | FXFQ25B
| Casette indoor unit (4.5 cooling / 5.0 heating ) |  |  |  | pcs | 3 |  | FXFQ40B
| Casette indoor unit (5.6 cooling / 6.3 heating ) |  |  |  | pcs | 2 |  | FXFQ50B
Refnets:
| Refnet branch piping kit KHRQ22M20T |  |  |  | pcs | 10 |  | Daikin or analog
| Refnet branch piping kit KHRQ22M64T |  |  |  | pcs | 1
Cu pipes insulated:
| Ø6.4 |  |  |  | m | 72
| Ø9.5 |  |  |  | m | 89
| Ø12.7 |  |  |  | m | 102
| Ø15.9 |  |  |  | m | 89
| Ø28.6 |  |  |  | m | 30
| Extra refregerent charge R410A |  |  |  | kg | 11
Split system (with thermostats/control system in the kit):
Outdoor units:
| Split outdoor unit (6,0 KW cooling / 7,0 KW heating) | [6 empty] | RXS60L
Indoor units:
| Split duct indoor unit (6,0 KW cooling / 7,0 KW heating) | [6 empty] | FDXM60F3
Cu pipes insulated:
| Ø6.4 |  |  |  | m | 8
| Ø12.7 |  |  |  | m | 8
Radiator electrical:
| P=500 W |  |  |  | pcs | 1
| P=700 W |  |  |  | pcs | 1
| P=800 W |  |  |  | pcs | 2
| P=1000 W |  |  |  | pcs | 3
Additional materials 5% of cost