Delivery and installation of flow measurement system on Zhinvali HPP

Zhinvali HPP General Data

The Zhinvali HPP consists of a 520 mio m3 reservoir retained by an embankment dam on the Aragvi

River.

Head 170 m water head and a 130 MW power plant. The scheme was commissioned in 1985.

The main characteristics of the project are the following :

Hydrology

- Average river flow at intake 43.8 m3/s

Dam

- Type Earth dam

- Structure With central clayey core

- Material Gravels and clay

- Foundation soil Conglomerate

Reservoir

- Function Seasonal water storage

- Normal water level 810 masl

- Minimum operational level 770 masl

Spillway

- Type Ungated overflow spillway, open channel

- Location Left bank

- Elevation 810 masl

- Length 600 m

- Design flood 1'240 m3/s

Bottom outlet

- Type Tower

- Number of openings 2 (5.0 x 5.0 m2)

- Elevation 762.8 masl

- Capacity 1'080 m3/s

Water intake

- Type Tower

- Capacity 115 m3/s

- Protection Two gates (service / maintenance)

Penstock

- Operation mode Pressurized

- Location low level

- Material Reinforced concrete and steel lining

- Length 648 m

- Diameter 5'500 - 5'300 mm

HPP

- Number of Units 4

- Type of turbines Francis (vertical)

- Total installed power P = 4 X 32.5 MW= 130 MW

Energy

- Annual production 430 GWh

- Transformers 2 x 220 MVA + 1 x 110 MWA

- Power line 110 kV, 220 kV

The specification calls for  flow measurement systems for each  turbine:

- Flow measurement systems for each Turbine penstock section

- Supplier must be presentrd price for delivery and installation duration for 2 set of equipments and for 4 set of equipments.

- Required accuracy of these flowmeter were defined by Zhinvali HPP / GWP with 1% Transducer mount shall be in accordance with the IEC60041 / ASME PTC 18

# Technical datas

- Penstock diameter = 2.2m

- Valve fully open

- V = >0.5m/s

- Nominal pressure before the turbines: hydrostatic pressure, min - 13 bar

- Maximum pressure before the turbines: hydrostatic pressure, max - 17 bar

# Penstock Flow Measurement

## Scope of supply

- Flow measurement in the penstock

- Gross head 170 m.

- Discharge measurement 0-50 m3/s

- Control unit with integrated turbine efficiency monitoring

## Flow Measurement Methode

- The flow measurement method (like Ultrasonic transit time) and according IEC60041/ ASME PTC18 for turbine efficiency testing and monitoring and shall provide a possible accuracy of 1 % on the measured flow (Q) value.

- The meter shall allow at least the calculation methods associated with the type of measurement arrangement in full pipelines under pressure

## Applicable Standards

- IEC-60041(1991) - Tests of hydraulic turbines, accumulation pumps and pump-turbines, to determine their hydraulic performance.

- ASME PTC-18 (2011) - Hydraulic turbines and pump-turbines. Performance test codes.

## Design

- The flow measurement system design shall be according IEC60041/ ASME PTC18 a.

- Protection cover system shall be designed for a waterproof application.

## Communication & Interfaces

- The flowmeter must be able to be integrated into the Plant Distributed Control System (SCADA) directly through IEC 60870-5-104 protocol.

- The flowmeter must be able to be programmed by web-interface / web-browser, no proprietary software is accepted.

- Flow data transfer technology must be Ethernet with at least 10/100 BaseT -, protocol TCP/IP

- Flowmeter must include WIFI 802.11a/b/g/n or newer/faster

- Flowmeter must include 3G/4G cellular modem option

- Flowmeter must be available to integrate signal in Siemens PLC

- Each Flowmeter must be having LCD panel (where must be showed flow different data) and it is mandatory to save minimum 1-year history for each of measurements and this data must have possibility to convert in excel file.

## Warrantee

Warranty must be minimum 2 years on all products and installations.

| Flowmeter - Technical Data Specification |  |  |  |
| --- | --- | --- | --- |
| 1 | General |  | Requirements |
| 1.1 | Fluid Velocity Range |  | 0 m/s up to ±20 m/s (or more on request); bidirectional |
| 1.2 | Calculation of flow accordance |  | IEC-60041/ASME PTC18 |
| 1.3 | Flow data transfer technology |  | Ethernet port with at least 10/100 BaseT – TCP/IP |
| 1.4 | Transit Time |  | < 1ns |
| 1.5 | Minimum measuring range |  | 0-50 m3/s |
| 1.6 | User/parameterization interface |  | By web browser / no proprietary software accepted |
| 2 | Communication interfaces and protocols |  |  |
| 2.1 | Ethernet |  | Ethernet ports with at least 10/100BaseT |
| 2.2 | Wireless |  | WIFI 802.11a/b/g/n or newer/faster |
| 2.3 | Cellular |  | 3G/4G cellular modem option |
| 2.4 | Modbus RTU+RCP, Master+Slave |  | built in in the control unit (no external devices/interfaces accepted) |
| 2.5 | IEC 60870-5-104 |  | built in in the control unit (no external devices/interfaces accepted) |
| 2.6 | Security of all relevant external digital communication interfaces |  | SSL/TLS 1.3 or newer |
| 3 | Environmental conditions |  |  |
| 3.1 | Ambient temperature |  | -20 … +70 °C |
| 3.2 | Relative Humidity |  | 5-95 % @ 25 °C |
| 3.3 | Installation height |  | up to 1000 masl |
| 4 | Power supply |  |  |
| 4.1 | Rated voltage |  | 24-48VDC / 90-260 VAC |
| 5 | Analog and digital Signals (Outputs/Inputs) |  |  |
| 5.1 | Analog Outputs | min. No of Analog outputs 4-20 mA | 4 (more as an option) |
| 5.2 |  | Resolution (bits) | 16 |
| 5.3 |  | Accuracy 25°C | ±0.1 %FS |
| 5.4 |  | Linearity | ≤ 0.04 % FS |
| 5.5 |  | Temperature drift | ≤ 70 ppm/K |
| 5.6 |  | Galvanic isolation | Full galvanic isolation |
| 5.7 |  | Overload protection | Integrated |
| 5.8 | Analog Inputs | min. No of Analog inputs 4-20 mA | 3 (more as an option) |
| 5.9 |  | Galvanic isolation | Full galvanic isolation |
| 5.10 | Digital Outputs | Galvanic isolation | Full galvanic isolation |
| 5.11 |  | min. No of digital outputs 4-20 mA | 9 digital output relays with configurable switched contacts (more as an option) |
| 5.12 |  | Output type | Relay with NO/NC changeover contact or solid-state with comparable electrical characteristics |
| 5.13 | Digital Inputs | Galvanic isolation | Optically Isolated |
| 5.14 |  | min. No of digital inputs 4-20 mA | 1 (more as an option) |
| 6 | Flow Transducers |  |  |
| 6.1 | Number of Transducers |  | Up to 20 path system according layout & needed |
| 6.2 | Galvanic isolation |  | Full galvanic isolation |
| 6.3 | Separation of transducers to flow meters |  | up to 300m |
| 6.4 | Degree of protection |  | IP 68 |
| 6.5 | Maximum pressure |  | at least up to 80bar |
| 6.6 | Probe frequency |  | 1 MHz |
| 6.7 | Transducer Material |  | Stainless steel 316L |
| 6.8 | Water temperature range |  | -30 °C to +70 °C |
| 6.9 | Relative humidity range |  | 100% |
| 6.10 | Type/Way of installation |  | Mounting from inside or outside |