## Sheet1
Location: |  | Tbilisi, Gagarini str.29
CHILLER
|  | Summer Operation Outlet Air Conditition : | +38 ⁰C (DB) 30% RH
|  | Winter Operation Outlet Air Conditition : | -8 ⁰C (DB) 70% RH
With anti-freezing kit for winter (-14 ⁰C )
| 1 | Designation | CH-01&02 (2 chiller)
| 2 | Equipment Location | Outdoor
| 3 | Type | Cooling only chiller
| 4 | MIN Cooling Capacity (kW) | 420
|  | MAX Cooling Capacity (kW) | 500
| a. | Refrigerant | 100% water
| b. | Water Inlet Temperature (⁰C) | 12
| c. | Water Outlet Temperature (⁰C) | 7
| d. | EER (energy efficianty class B or more) | 2.9 or more
| 5 | Compressor
| a. | Type | Scroll
| 6 | Cooling Electric Data
| a. | Volt/Phase/Hertz | 400/3/50
Note:The offer should include the deinstallation and installation of the chiller, as well as the transportation of the secondary chiller to the warehouse.
Note: The offer should include testing and commision