## IO
Thickener area
| INSTRUMENT_TAG | PLC_TAG | DESCRIPTION | SIGNAL_TYPE |  | RANGE | POWER_SUPPLY
| 200-LIT-001 |  | Hydrocyclone Feed Tank Level Control | AI | 4-20 mA | 0 - 100 % | 24VDC | 2-wire connection
| 200-LIT-002 |  | Hydrocyclone Overflow Tank Level Control | AI | 4-20 mA | 0 - 100 % | 24VDC | 2-wire connection
| 200-FT-001 |  | Water Flow To Sag Mill | AI | 4-20 mA | 0 - 150 m3/hr | 24VDC | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Water Flow To Sag Mill (Totalizer) | DI | RIO is active | 1 pulse - 0.1 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| 200-FT-002 |  | Gland Seal Water Flow | AI | 4-20 mA | 0 - 30 m3/hr | 24VDC | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Gland Seal Water Flow (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| 200-FT-003 |  | Water Flow To Ball Mill | AI | 4-20 mA | 0 - 200 m3/hr | 24VDC | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Water Flow To Ball Mill (Totalizer) | DI | RIO is active | 1 pulse - 0.1 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| 200-FT-004 |  | Water Flow To Hydrocyclone Feed/Overflow Tanks | AI | 4-20 mA | 0 - 100 m3/hr | 24VDC | 2-wire power supply 24 V DC, 2-wire 4-20 mA connection (Instrument is active), Pulse output (2-wire connection)
|  |  | Water Flow To Hydrocyclone Feed/Overflow Tanks (Totalizer) | DI | RIO is active | 1 pulse - 0.1 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| 200-PIT-001 |  | Instrument Air Pressure Control | AI | 4-20 mA |  | 24VDC | 2-wire connection
| 200-PP-005SP |  | Gland Seal Pump 200-PP-005 Frequency Set Point | AO | 4-20 mA |  | 24VDC | 2-wire connection
| 200-PP-006SP |  | Gland Seal Pump 200-PP-006 Frequency Set Point | AO | 4-20 mA |  | 24VDC | 2-wire connection
| 100-AP-001 |  | Aprone Feeders in Local / Remote Mode | DI |  |  | 24VDC | 2-wire connection
| 200-FV-023 |  | 200-PP-001 Inlet Valve | DI |  |  | 24VDC | Closed Status | pneumatic actuated, 2-coils solenoid
|  |  | 200-PP-001 Inlet Valve | DI |  |  | 24VDC | Opened Status
|  |  | 200-PP-001 Inlet Valve | DO | + 24 V from module |  | 24VDC | Close Command
|  |  | 200-PP-001 Inlet Valve | DO | + 24 V from module |  | 24VDC | Open Command
| 200-FV-024 |  | 200-PP-002 Inlet Valve | DI |  |  | 24VDC | Closed Status | pneumatic actuated, 2-coils solenoid
|  |  | 200-PP-002 Inlet Valve | DI |  |  | 24VDC | Opened Status
|  |  | 200-PP-002 Inlet Valve | DO | + 24 V from module |  | 24VDC | Close Command
|  |  | 200-PP-002 Inlet Valve | DO | + 24 V from module |  | 24VDC | Open Command
| 200-FV-025 |  | 200-PP-003 Inlet Valve | DI |  |  | 24VDC | Closed Status | pneumatic actuated, 2-coils solenoid
|  |  | 200-PP-003 Inlet Valve | DI |  |  | 24VDC | Opened Status
|  |  | 200-PP-003 Inlet Valve | DO | + 24 V from module |  | 24VDC | Close Command
|  |  | 200-PP-003 Inlet Valve | DO | + 24 V from module |  | 24VDC | Open Command
| 20-FV-012 |  | 200-PP-003 Outlet Valve | DI |  |  | 24VDC | Closed Status | pneumatic actuated, 2-coils solenoid
|  |  | 200-PP-003 Outlet Valve | DI |  |  | 24VDC | Opened Status
|  |  | 200-PP-003 Outlet Valve | DO | + 24 V from module |  | 24VDC | Close Command
|  |  | 200-PP-003 Outlet Valve | DO | + 24 V from module |  | 24VDC | Open Command
| 200-FV-026 |  | 200-PP-004 Inlet Valve | DI |  |  | 24VDC | Closed Status | pneumatic actuated, 2-coils solenoid
|  |  | 200-PP-004 Inlet Valve | DI |  |  | 24VDC | Opened Status
|  |  | 200-PP-004 Inlet Valve | DO | + 24 V from module |  | 24VDC | Close Command
|  |  | 200-PP-004 Inlet Valve | DO | + 24 V from module |  | 24VDC | Open Command
| 20-FV-022 |  | 200-PP-004 Outlet Valve | DI |  |  | 24VDC | Closed Status | pneumatic actuated, 2-coils solenoid
|  |  | 200-PP-004 Outlet Valve | DI |  |  | 24VDC | Opened Status
|  |  | 200-PP-004 Outlet Valve | DO | + 24 V from module |  | 24VDC | Close Command
|  |  | 200-PP-004 Outlet Valve | DO | + 24 V from module |  | 24VDC | Open Command
| 100-XS-006 |  | 100-CV-003 Belt Misalignment Switch | DI |  |  | 24VDC | Dry Contact
| 100-XS-007 |  | 100-CV-003 Pull Cord Switch | DI |  |  | 24VDC | Dry Contact
| 100-SA-003 |  | 100-CV-003 Zero Speed Sensor | DI | + 24 V from module |  | 24VDC | 2-wire connection
| 100-CV-003-SRN |  | 100-CV-003 Siren | DO | + 24 V from module |  | 24VDC | 2-wire connection
| 200-XS-001 |  | 200-CV-001 Belt Misalignment Switch | DI |  |  | 24VDC | Dry Contact
| 200-XS-004 |  | 200-CV-001 Pull Cord Switch | DI |  |  | 24VDC | Dry Contact
| 200-SA-001 |  | 200-CV-001 Zero Speed Sensor | DI | + 24 V from module |  | 24VDC | 2-wire connection
| 200-CV-001-SRN |  | 200-CV-001 Siren | DO | + 24 V from module |  | 24VDC | 2-wire connection
| 200-XS-002 |  | 200-CV-003 Belt Misalignment Switch | DI |  |  | 24VDC | Dry Contact
| 200-XS-005 |  | 200-CV-003 Pull Cord Switch | DI |  |  | 24VDC | Dry Contact
| 200-SA-002 |  | 200-CV-003 Zero Speed Sensor | DI | + 24 V from module |  | 24VDC | 2-wire connection
| 200-CV-003-SRN |  | 200-CV-003 Siren | DO | + 24 V from module |  | 24VDC | 2-wire connection
| 200-XS-003 |  | 200-CV-002 Belt Misalignment Switch | DI |  |  | 24VDC | Dry Contact
| 200-XS-006 |  | 200-CV-002 Pull Cord Switch | DI |  |  | 24VDC | Dry Contact
| 200-SA-003 |  | 200-CV-002 Zero Speed Sensor | DI | + 24 V from module |  | 24VDC | 2-wire connection
| 200-CV-002-SRN |  | 200-CV-002 Siren | DO | + 24 V from module |  | 24VDC | 2-wire connection