## Order.1856
ტექნიკური ნაწილი
1 | ზოგადსისტემური პანელი | 1783-CMS10DP Stratix 5200 switch, 8 copper 100/1000 ports, 2 Combo 100/1000 ports, full FW, DLR – 1, PLX32-EIP-MBTCP EtherNet/IP to Modbus TCP/IP Communication Gateway- 1, PLX32-EIP-PND EtherNet/IP to PROFINET Communication Gateway -2, 5094-AEN2TR EtherNet Adapter supports up to 16 local I/O modules (includes (1) 5094-AENRTB: 5094 Adapter RTB - Screw type – 1, 5094-IF8 Analog input, 8-channel – 2, 5094-OF8 Analog output, 8-channel – 1, 5094-MB Mounting base - 3, 5094-RTB3S Removable Terminal Block - Spring type – 3, 5094-MB Mounting base - 6, 5094-IB32 Digital input 24V DC, 32-point sinking digital input – 2, 5094-RTB32VS 32-point Removable Terminal Block - Spring type – 2, 5094-OB32 Digital output 24V DC, 32-point sourcing digital output – 2, 5094-RTB32CS 32-point Removable Terminal Block - Spring type – 2, Finder relay Type 93 "10 last spare digital inputs should be galvanically isolated with relays with 24 V DC coils; 10 last digital outputs should be galvanically isolated with relays with 24 V DC coils;" - 20, Cabinet IP rating IP55, Power supply 220 V AC 1ph from UPS, DC Power Source 24 V DC Power supply (20 A), Lighting, Terminals Spring loaded type, 2,5 mm2 wire max, fuse protection for +24V terminal in each control/instrumentation loop, Mounting Wall-mounted, Dimensions Approximately 1200 x 1200 x 350 mm, 2 doors, Material "Enclosure: Sheet steel 1.5 mm, Door: Sheet steel, 2.0 mm, Rear panel: Sheet steel, 1.5 mm, Gland plates: Sheet steel, 1.5 mm, Mounting plate: Sheet steel, 3.0 mm", Surface finish Enclosure, door and rear panel: dipcoat-primed, powder-coated on the outside, textured paint Mounting plate and gland plates: Zinc-plated, Color RAL7035, Earthing 2 independent ground bars (electrical and instrumentation earthing), Cable entrance Bottom, Cooling system 1 FAN with dust filter | ცალი | 1