### Terms of Reference (ToR) for the Rehabilitation and Upgrade of Zhinvali HPP Monitoring Systems

#### 1. Introduction

The Zhinvali Hydropower Plant (HPP) is a critical infrastructure asset that plays a vital role in energy production and water management in the region. Over the years, various monitoring systems have been installed to ensure the operational safety and structural integrity of the dam. These systems include the Central Data Acquisition and Communication Network, Piezometric Network, Seepage Monitoring System, Meteorological Station, Horizontal and Vertical Deformation Monitoring System, Mechanical Crackmeters, Seismic Network, Water Level Monitoring System, Tailrace Tunnel Monitoring System, and Temperature Monitoring System.

A recent comprehensive technical inspection has highlighted several inefficiencies and areas in need of improvement within these monitoring systems. To address these issues and enhance the overall reliability and effectiveness of the dam's monitoring infrastructure, a targeted rehabilitation and upgrade project is proposed.

The objective of this project is to implement the necessary technical measures for the rehabilitation and upgrade of the monitoring systems at Zhinvali HPP. This will ensure the continued operational safety of the dam and improve the accuracy and reliability of the data collected for early warning and monitoring purposes.

The scope of this project includes a site visit (if applicable) and subsequent rehabilitation and upgrade of each monitoring system in accordance to this TOR. The project aims to address the specific technical deficiencies identified during the inspection (inspection report is available based on submission of respective NDA), integrate autonomous systems, automate manual processes, mitigate signal interferences, and enhance the overall data acquisition and communication network.

This document provides the Terms of Reference (ToR) and the Bill of Quantities (BoQ) required for the rehabilitation and upgrade project, detailing the scope of work, deliverables, timeline, budget, and evaluation criteria. The successful implementation of this project will significantly augment the monitoring capabilities at Zhinvali HPP, ensuring its long-term safety and operational efficiency.

#### 2. Instrumentation and Systems Components and Quantities (existing equipment and devices)

Components and Quantities of the Instrumentation and Systems

| Item | Quantity | Description |
| --- | --- | --- |
| Pressure Transducers | 24 | Used in the grouting gallery to monitor the effectiveness of the dam grouting curtain |
| Standpipe VW Piezometers | 22 | Located in the dam body for monitoring water levels |
| DSM Control Points | 7 | On dam crest for differential settlement monitoring |
| Biaxial Clinometers | 16 | For monitoring inclinations and horizontal displacement at dam crest, spillway, outlet, intake structures |
| Seismic Stations (SMR) | 7 | In the dam body |
| Automated Meteorological Station | 1 | For weather monitoring |
| Seepage and Drainage Weirs | 2 | For measuring water flow |
| Radar-type Water Level Gauge | 1 | On water intake structure for automated water level monitoring |
| Crackmeters | 15 | 6 of them are specified models from the current monitoring system |
| Two-point MEXID Extensometers | 8 | For monitoring deformations in the tunnel lining and surrounding soil |
| VW Temperature Sensors | 4 | For measuring water temperature in the reservoir |
| Shaft Encoder | 2 | For measuring the position of the shafts |
| ADK 100 | 2 | Data acquisition systems |
| Cr 1000 | 1 | Data acquisition system |
| Syscom NCC | 1 | For acquiring seismic data |

#### 3. Inspection Outcomes and Scope of Works

##### 3.1 Central Data Acquisition and Communication Network

Outcomes:

- The network has inefficiencies and needs improvement in integration and automation.

- Signal interference, particularly from nearby high voltage lines, is an issue.

Recommendations:

- Integrate autonomous systems into the centralized data analysis platform.

- Enhance automation of manual systems.

- Mitigate signal interference by installing intermediary dataloggers at switch terminal boxes.

- Explore additional or alternative connectivity options due to past damages to fiber optic cables.

##### 3.2 Piezometric Network

Outcomes:

- Several monitoring points were missing identification cards, and some mechanical manometers needed replacement.

- High variance in measurement values due to electrical interference from multicore cable routing through the sub-station yard.

Recommendations:

- Update identification plates for all instruments.

- Replace malfunctioning mechanical manometers.

- Improve the commutation scheme by deploying autonomous LoRa wireless nodes to eliminate electromagnetic interferences.

##### 3.3 Seepage Monitoring System

Outcomes:

- Inspection revealed the need for systematic maintenance and modernization.

- Water sampling locations were evaluated, and the strategy was reassessed.

Recommendations:

- Implement a maintenance plan for the stations.

- Optimize water sampling procedures and laboratory analysis (optional)

- Modernize and automate seepage monitoring stations with wireless nodes.

- Install ultrasonic clamp-on flow meters for continuous monitoring of seepage flow rates.

##### 3.4 Meteorological Station

Outcomes:

- The station’s battery and wind speed sensor were malfunctioning.

- The station is over ten years old, with many components significantly aged.

Recommendations:

- Replace the entire meteorological station with modern, maintenance-free instruments.

- Alternatively, replace only the damaged components, although this does not address the potential failure of other aged components.

##### 3.5 Horizontal and Vertical Deformation Monitoring System

Outcomes:

- Inconsistencies were found, likely due to mechanical damage from previous construction activities.

- Differential settlement sensors exhibited abnormal readings.

Recommendations:

- Undertake targeted rehabilitation of the system.

- Replace sensors with advanced-generation instruments.

- Maintain or modify geodetic leveling marks to ensure integrity for further surveys.

##### 3.6 Mechanical Crackmeters

Outcomes:

- Outdated manual measuring devices needed replacement.

- 3D mechanical crack-meters showed unstable installation.

Recommendations:

- Upgrade measurement methodology and hardware.

- Stabilize 3D crack-meters or reinstall for correct usage.

- Automate monitoring of joints and cracks on the gravity dam.

##### 3.7 Seismic Network

Outcomes:

- Time synchronization issues due to GPS antenna problems.

- Component failures in the autonomous power supply units.

Recommendations:

- Replace malfunctioning GPS units and recommission the system.

- Consider replacing the entire seismic monitoring network with advanced technology.

- Integrate the new system with the central data logging unit.

##### 3.8 Water Level Monitoring System

Outcomes:

- Critical failure in December 2023 due to optical cable damage, interrupting data transmission.

Recommendations:

- Implement redundancy measures within the monitoring infrastructure.

- Add an extra reservoir water level sensor to ensure continuous monitoring.

##### 3.9 Tailrace Tunnel Monitoring System

Outcomes:

- GSM modem for data telemetry failed, necessitating replacement.

Recommendations:

- Replace the failed modem and integrate the system with the central control room for streamlined data management.

##### 3.10 Temperature Monitoring System

Outcomes:

- General need for regular maintenance and potential replacement of outdated components.

Recommendations:

- Ensure regular maintenance and inspection.

- Replace outdated components and integrate the system for automated monitoring.

##### 3.11 Early Warning System (EWS)

Outcomes:

- Power supply and batteries were significantly aged and mostly malfunctioning.

- Damage to some cables in the EWS control room, likely caused by rodents.

- Proper operability of the system could not be verified due to these issues.

Recommendations:

- Comprehensive rehabilitation of the EWS's power supply and peripheral components.

- Immediate and systematic preventive measures to address rodent damage.

- Detailed technical inspection and testing of the entire EWS system in collaboration with the system's manufacturer to ensure proper functionality.

4. Key Technical Specifications of the Deliverable Instrumentation

| Technical Specification | Value |
| --- | --- |
| Central Data Acquisition Unit for Radio Communication Transceiver |  |
| Radio and Network interfaces | ISM Sub GHz 2.6dBi Antenna -137 dBm Sensitivity Long range communication (up to 15km) 4G Modem with worldwide LTE 10/100 Ethernet WAN (RJ45 PoE) Embedded Web Interface with Remote Access over LTE (Non-Static SIM) |
| Mechanical Properties | IP67 -40 to +60 °C Min. button(s) for On/Off/Reset RJ45 and USB-C Port |
| Power Supply | PoE 802.3af 5V through USB C or similar 5.1 V DC, 1.2A max or similar |
| Piezometric Network of Dam and Gallery |  |
| Node Radio and Network interfaces | ISM sub GHz LoRa/ LoRaWAN 151 dB / 157 dB Long range communication (up to 15km) 200 000 readings Memory / 1 Channel |
| Node Mechanical Properties | IP68 -40⁰C to 80⁰C Grounding connector and Surge protection USB to PC port |
| Node Measurement Method | Vibrating Wire, 300 to 7 000 Hz |
| Power Supply | 3.6V C-Size battery or similar |
| Seepage Monitoring System |  |
| Measurement Type | Automatic Level Station and Flow Measurement Station |
| Measurement Method and Accuracy | Level Measurement Radar or Pressure Transducer 1-Meter Range with 1mm Accuracy Flow Measurement Electromagnetic ± 2% Flow Measurement Accuracy |
| Mechanical Properties | IP67 316 Stainless Steel Material or similar |
| Node Radio and Network interfaces | ISM sub GHz LoRa/ LoRaWAN 151 dB / 157 dB Long range communication (up to 15km) 200 000 readings Memory / 1 Channel |
| Horizontal and Vertical Deformation Monitoring System |  |
| Measurement Type | Hydraulically Connected Gauges connected to a Reference Tank 7 Measurement stations Along the Dam Automatic Datalogging with Telemetry Geodetic Monitoring Accessories for Reference Geodetic Observations |
| Measurement Method and Accuracy | Capacitive ceramic pressure sensor Min. 500 mm H2O Range ±0.07% FS or similar 0.002% FS Resolution or better RS-485, Modbus RTU protocol Output Signal |
| Mechanical Properties | IP67 -20°C to +70°C |
| Mechanical Crackmeters |  |
| Node Radio and Network interfaces | ISM sub GHz LoRa/ LoRaWAN 151 dB / 157 dB Long range communication (up to 15km) 200 000 readings Memory / 1 Channel |
| Node and Sensor Mechanical Properties | Node - IP68, USB to PC port, Grounding connector and Surge protection Sensor - Up to 1 MPa, Concrete Embedded Type Sensor -20⁰C to 80⁰C |
| Node and Sensor Measurement Method and Accuracy | Vibrating Wire , 300 to 7 000 Hz 25/50 mm Range ±0.5%FS Accuracy |
| Power Supply | 3.6V C-Size battery or similar |
| Redundant Water Level Monitoring System |  |
| Measurement Type | Pressure Transducer, 50m range 4...20 mA or MODBUS RTU Output Signal |
| Measurement Method and Accuracy | 0.1% FS Accuracy or better |
| Meteorological Station |  |
| Mechanical Properties | IP66 -35 to +60°C |
| Communication Interface | SDI-12, RS-232, RS-485, RS-422 SDI 12 v1.3, Modbus RTU, ASCII, NMEA 0183 v3.0 |
| Air Temperature and Humidity | −35 … +60 °C and 0 … 100 %RH ±0.3 °C and ±3 %RH @ 0 … 90 %RH |
| Atmospheric Pressure | 500 … 1100 hPa ±0.5 hPa @ 0 … +30 °C |
| Wind Speed and Direction | 0 … 60 m/s and 0 … 360° ±3 % and ±3.0° @ 10 m/s |
| Precipitation | Tipping Bucket Type with Heater Liquid and Solid type of Precipitation Measurement 200 cm2 Collection Area |
| Node Radio and Network interfaces | ISM sub GHz LoRa/ LoRaWAN 151 dB / 157 dB Long range communication (up to 15km) |

### 5. Bill of Quantities (BoQ)

| # | Type of Instrument or System | QTY | Unit Price (EUR) | Total Price (EUR) |
| --- | --- | --- | --- | --- |
| 1 | Central Data Acquisition Unit for Radio Communication Transceiver |  |  |  |
| 1.1 | Supply of Radio Gateway with Accessories | 1 |  |  |
| 1.2 | Installation, Configuration and Testing of Data Gateway | 1 |  |  |
| 2 | Piezometric Network of Dam and Gallery |  |  |  |
| 2.1 | Supply of Radio Node with Accessories | 10 |  |  |
| 2.2 | Supply of Water Level Indicator 100m | 1 |  |  |
| 2.3 | Installation, Configuration and Testing of Nodes | 10 |  |  |
| 3 | Seepage Monitoring System |  |  |  |
| 3.1 | Supply of Automatic Level Measurement Sensor | 2 |  |  |
| 3.2 | Supply of Radio Node for Level Sensor | 2 |  |  |
| 3.3 | Supply of Flow Meter for the Water Supply Pipe | 1 |  |  |
| 3.4 | Installation, Configuration and Testing of Level Measurement Systems at Seepage Channels | 2 |  |  |
| 4.5 | Installation, Configuration and Testing of Flow Measurement System of Water Supply Pipe | 1 |  |  |
| 4 | Horizontal and Vertical Deformation Monitoring System |  |  |  |
| 4.1 | Supply of Reference Leveling Station | 1 |  |  |
| 4.2 | Supply of Monitoring Leveling Station | 7 |  |  |
| 4.3 | Supply of Geodetic Monitoring Network Accessories (leveling marks..) | 8 |  |  |
| 4.4 | Installation, Configuration and Testing of Deformation Monitoring Stations | 8 |  |  |
| 5 | Mechanical Crackmeters |  |  |  |
| 5.1 | Supply of Electric Embedded Jointmeter with Cable | 5 |  |  |
| 5.2 | Supply of Radio Nodes of Jointmeters | 5 |  |  |
| 5.3 | Installation, Configuration and Testing of Crackmeters Network | 5 |  |  |
| 6 | Redundant Water Level Monitoring System |  |  |  |
| 6.1 | Supply of Water Level Sensor with Cable for Laminographic Pipe | 1 |  |  |
| 6.2 | Supply of Water Level Sensor Node | 1 |  |  |
| 6.3 | Installation, Configuration and Testing of Redundant Water Level System | 1 |  |  |
| 7 | Meteorological Station |  |  |  |
| 7.1 | Supply of Meteorological Station | 1 |  |  |
| 7.2 | Supply of Meteorological Station Node | 1 |  |  |
| 7.3 | Installation, Configuration and Testing of Meteorological Station | 1 |  |  |
| 8 | Seismic Network |  |  |  |
| 8.1 | Manufacturer System Inspection and Report for GPS time synchronization and etc. | 5 |  |  |
| 8.2 | Rehabilitation of Peripherals and Commissioning | 7 |  |  |
| 8.3 | Recommendation to Improve and Modernize Seismic Network | 1 |  |  |
| 9 | Tailrace Tunnel Monitoring System |  |  |  |
| 9.1 | Replace GSM Modem of the Existing System | 1 |  |  |
| 9.2 | Reconfiguration and Commissioning | 1 |  |  |
| 10 | Early Warning System |  |  |  |
| 10.1 | Rehabilitation of Peripheral Components | 6 |  |  |
| 10.2 | Comprehensive Inspection to Issue the Detailed Recommendations | 1 |  |  |
| 10.3 | Scheduling the Detailed Agenda for Systematic Checking and Testing of the EWS | 1 |  |  |
| 11 | System Commissioning and Reporting |  |  |  |
| 11.1 | Final Configuration and Commissioning of the Monitoring Network | 1 |  |  |
| 11.2 | As-built Documentation and Final Reporting | 1 |  |  |

Note: Please fill in the unit cost and total cost based on actual pricing or quotations from suppliers.

This detailed BoQ ensures that all tasks and components necessary for the rehabilitation and upgrade of the Zhinvali HPP monitoring systems are accounted for, facilitating accurate budgeting and efficient project execution.