Delivery and installation of flow measurement device on Zhinvali Tailrace tunnel.

Zhinvali tailrace Tunnel is free flow tunnel, it is necessary to install flow measurement device on CH 0+50 to CH 2+00, installation place must be choose by supplier.

- Tunnel dimensions are seen below.

In annex N1 please see tunnel drawing;

- Measurement ranges as follows:

Maximun flow : 70m3/s

Minimun flow: 15 m3/s

Average: 25 m3/s

- Instalation place, tailrace tunnel of Zhinvali HPP

- Water from Big DUM of HPP to the tailrace tunnel.

- No Risk of sediment.

- Tunnel is from concrete

- Min. expected temperature: 6 °C

- Max. expected temperature: 16 °C

- It is mandatory that measurement accuracy must be not more than 5% .

- There must be installed combination of different measurements as a ultrasonic transit time and or other kind of equipment to achieve lower 5% of accuracy.

- Installation must be finished during tunnel stoppage period, 15 May-15 June 2025 year.

| Flowmeter - Technical Data Specification |  |  |  |
| --- | --- | --- | --- |
| 1 | General |  | Requirements |
| 1.1 | Flow data transfer technology |  | Ethernet port with at least 10/100 BaseT – TCP/IP |
| 1.2 | Transit Time |  | < 1ns |
| 1.3 | User/parameterization interface |  | By web browser / no proprietary software accepted |
| 2 | Communication interfaces and protocols |  |  |
| 2.1 | Ethernet |  | Ethernet ports with at least 10/100BaseT |
| 2.2 | Wireless |  | WIFI 802.11a/b/g/n or newer/faster |
| 2.4 | Modbus RTU+RCP, Master+Slave |  | built in in the control unit (no external devices/interfaces accepted) |
| 2.5 | IEC 60870-5-104 |  | built in in the control unit (no external devices/interfaces accepted) |
| 2.6 | Security of all relevant external digital communication interfaces |  | SSL/TLS 1.3 or newer |
| 3 | Environmental conditions |  |  |
| 3.1 | Ambient temperature |  | -20 … +70 °C |
| 3.2 | Relative Humidity |  | 5-95 % @ 25 °C |
| 3.3 | Installation height |  | up to 1000 masl |
| 4 | Power supply |  |  |
| 4.1 | Rated voltage |  | 24-48VDC / 90-260 VAC |
| 6 | Flow Transducers |  |  |
| 6.1 | Degree of protection |  | IP 68 |
| 6.2 | Pressure |  | freeflow tunnel |
| 6.3 | Water temperature range |  | -15 °C to + 40 °C |
| 6.4 | Relative humidity range |  | 100% |
| 6.5 | Type/Way of installation |  | Mounting from inside or outside |