## Sheet2 (hidden)
COSTING SHEET
[6 empty] | MATERIAL |  |  |  | LABOUR
Si No: | Description | Qty | Uom | Rate | Amount | BASIC PRICE | OH@8% | MARGIN @12% | TOTAL RATE | BASIC PRICE | OH@8% | MARGIN @12% | TOTAL RATE | #REF!
1 | DUCTING (G.I. SHEET) - SUPPLY, RETURN, FRESH AND EXTRACT AIR DUCTING COMPLETE WITH ALL RELATED ACCESSORIES E.G. SUPPORTS HANGERS FLEX. CONNECTIONS, TEST HOLES, ACCESS PANELS. |  |  | 0 | 0 | 0 |  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 24G | 1 | SQ.MTR | 73.365 | 73.365 | 42.5833 | 3.4067 | 5.11 | 51.1 | 18.25 | 1.825 | 2.19 | 22.265 | 73.365 | 0 | 51.3555 | 22.0095 | 42.7962 | 18.3412
| 22G | 1 | SQ.MTR | 73 | 73 | 42.5833 | 3.4067 | 5.11 | 51.1 | 18.25 | 1.46 | 2.19 | 21.9 | 73 | 0 | 51.1 | 21.9 | 42.5833 | 18.25
H | SITC of EXTRACTS FOR VENTILATION FANS | 14 | NOS | 4774 | 66836 | [8 empty] | 0 | -4774

## Break up details-Chemo (hidden)
5031.15
SL No. | location | Type | Duct size - mm |  |  |  | Length in mm | Insulation type | Sheet thickness & Area sqmtr. | 22 G | 20 G | 18 G | Acoustic area Sft. | Thermal area Sqmt | Remarks
|  |  | W1 | H1 | W2 | H2 |  |  | 24 G | 22 G | 20 G | 18 G | Thk. Inch | Thk.mm
[8 empty] | A/T | [5 empty] | 9 | Remarks
ALZAHARA -CHEMO AREA DUCT Measurement
TOTAL QUANITITY | [6 empty] | 44008 |  | 73.3265 | 0 | 0 | 0 | 0 | 75.3717
FRESH AIR DUCT
1 | Waiting Area | 1 | 650 | 200 |  |  | 5919 | T | 10.0623 |  |  |  | T | 10.4885
2 |  | 1 | 650 | 200 |  |  | 956 | T | 1.6252
3 |  | 1 | 650 | 200 |  |  | 348 | T | 0.5916 |  |  |  | T | 0.61666
4 |  | 3 | 650 | 200 |  |  |  | T | 1.269 |  |  |  | T | 1.3227
5 |  | 1 | 650 | 200 |  |  | 592 | T | 1.0064 |  |  |  | T | 1.049
EXHAUST AIR DUCT
1 |  | 1 | 550 | 250 |  |  | 645 | T | 1.032 |  |  |  | T | 1.0784
2 |  | 1 | 550 | 250 |  |  | 8605 | T | 13.768 |  |  |  | T | 14.3876
3 |  | 2 | 550 | 250 | 400 | 250 | 392 | T | 0.5684 |  |  |  | T | 0.59662
4 |  | 1 | 400 | 250 |  |  | 3451 | T | 4.4863 |  |  |  | T | 4.7348
5 |  | 2 | 400 | 250 | 400 | 200 | 171 | T | 0.21375 |  |  |  | T | 0.22606
6 |  | 1 | 400 | 200 |  |  | 2462 | T | 2.9544 |  |  |  | T | 3.1317
7 |  | 3 | 400 | 200 |  |  |  | T | 0.66003 |  |  |  | T | 0.69963
8 |  | 1 | 400 | 200 |  |  | 66 | T | 0.0792 |  |  |  | T | 0.083952
9 |  | 2 | 400 | 200 | 400 | 150 | 149 | T | 0.17135 |  |  |  | T | 0.18208
10 |  | 1 | 400 | 150 |  |  | 1535 | T | 1.6885 |  |  |  | T | 1.799
11 |  | 3 | 400 | 150 |  |  |  | T | 0.60503 |  |  |  | T | 0.64463
12 |  | 1 | 400 | 150 |  |  | 3273 | T | 3.6003 |  |  |  | T | 3.836
13 |  | 1 | 400 | 150 |  |  | 1300 | T | 1.43 |  |  |  | T | 1.5236
14 |  | 3 | 400 | 150 |  |  |  | T | 0.60503 |  |  |  | T | 0.64463
15 |  | 1 | 400 | 150 |  |  | 625 | T | 0.6875 |  |  |  | T | 0.7325
16 |  | 1 | 350 | 100 |  |  | 695 | T | 0.6255 |  |  |  | T | 0.67554
17 |  | 1 | 400 | 100 |  |  | 890 | T | 0.89 |  |  |  | T | 0.95408
| SUPPLY AIR DUCT | [6 empty] | T | 0 |  |  |  | T | 0
1 | 8 TR AHU | [6 empty] | T | 0 |  |  |  | T | 0
2 |  | 1 | 650 | 200 |  |  | 195 | T | 0.3315 |  |  |  | T | 0.34554
3 |  | 3 | 650 | 200 |  |  |  | T | 1.269 |  |  |  | T | 1.3227
4 |  | 1 | 650 | 200 |  |  | 665 | T | 1.1305 |  |  |  | T | 1.1784
5 |  | 1 | 650 | 200 |  |  | 700 | T | 1.19 |  |  |  | T | 1.2404
6 |  | 2 | 650 | 200 | 550 | 200 | 131 | T | 0.2096 |  |  |  | T | 0.21903
7 |  | 1 | 550 | 200 |  |  | 1770 | T | 2.655 |  |  |  | T | 2.7824
8 |  | 3 | 400 | 200 |  |  |  | T | 0.66003 |  |  |  | T | 0.69963
9 |  | 3 | 400 | 200 |  |  |  | T | 0.66003 |  |  |  | T | 0.69963
10 |  | 1 | 400 | 200 |  |  | 1155 | T | 1.386 |  |  |  | T | 1.4692
11 |  | 2 | 400 | 200 | 350 | 150 | 131 | T | 0.1441 |  |  |  | T | 0.15353
12 |  | 1 | 350 | 150 |  |  | 2270 | T | 2.27 |  |  |  | T | 2.4334
13 |  | 2 | 350 | 150 | 150 | 150 | 250 | T | 0.2 |  |  |  | T | 0.218
14 |  | 2 | 350 | 150 | 150 | 150 | 250 | T | 0.2 |  |  |  | T | 0.218
15 |  | 1 | 350 | 150 |  |  | 1300 | T | 1.3 |  |  |  | T | 1.3936
16 |  | 2 | 550 | 150 | 450 | 150 | 146 | T | 0.1898 |  |  |  | T | 0.20031
17 |  | 1 | 450 | 150 |  |  | 270 | T | 0.324 |  |  |  | T | 0.34344
18 |  | 2 | 450 | 150 | 162 | 150 | 269 | T | 0.24533 |  |  |  | T | 0.2647
19 |  | 2 | 450 | 150 | 162 | 150 | 269 | T | 0.24533 |  |  |  | T | 0.2647
20 |  | 3 | 450 | 150 |  |  |  | T | 0.70717 |  |  |  | T | 0.74961
21 |  | 1 | 450 | 150 |  |  | 545 | T | 0.654 |  |  |  | T | 0.69324
22 |  | 2 | 350 | 150 | 162 | 150 | 140 | T | 0.11368 |  |  |  | T | 0.12376
23 |  | 2 | 350 | 150 | 270 | 150 | 72 | T | 0.06624 |  |  |  | T | 0.071424
24 |  | 1 | 350 | 150 |  |  | 105 | T | 0.105 |  |  |  | T | 0.11256
25 |  | 3 | 350 | 150 |  |  |  | T | 0.51074 |  |  |  | T | 0.54751
26 |  | 1 | 350 | 150 |  |  | 380 | T | 0.38 |  |  |  | T | 0.40736
27 |  | 2 | 400 | 150 | 350 | 150 | 141 | T | 0.14805 |  |  |  | T | 0.1582
28 |  | 1 | 350 | 150 |  |  | 62 | T | 0.062 |  |  |  | T | 0.066464
29 |  | 2 | 350 | 150 | 162 | 150 | 121 | T | 0.098252 |  |  |  | T | 0.10696
30 |  | 2 | 350 | 150 | 162 | 150 | 62 | T | 0.050344 |  |  |  | T | 0.054808
31 |  | 1 | 350 | 150 |  |  | 535 | T | 0.535 |  |  |  | T | 0.57352
|  |  | 650 | 200 |  |  | 100 |  | 0.17
|  |  | 400 | 150 |  |  | 100 |  | 0.11
|  |  | 350 | 100 |  |  | 100 |  | 0.09
|  |  | 400 | 150 |  |  | 100 |  | 0.11
|  |  | 400 | 150 |  |  | 100 |  | 0.11
|  |  | 400 | 150 |  |  | 100 |  | 0.11
|  |  | 500 | 250 |  |  | 150 |  | 0.225
|  |  | 730 | 200 |  |  | 150 |  | 0.279
Total Qty
| Mtrs suppuort | Nos.
| 44.008 | 22.004 | Thraeded Rod | 2 | Rmtrs | 8.5596 | 0.389 | 9.4155
|  |  | nut washer 8 mm | 4 | nos | 88.016 |  | 96.8176
|  |  | slotted channel | 2 | no.s | 44.008 |  | 48.4088
|  |  | anchor fastner | 2 | nos | 44.008 |  | 48.4088

## RA-CHEMO AREA (hidden)
1 | HVAC works
RATE ANALYSIS
| Dsecription | Uom | Qty | Rate (INR) | Rate (AED) | Remarks
1.3 | Supply, fix, balance, and commission louvre type smooth Volume control damper made of extruded aluminium linkage, lever, fixing arrangement etc.complete brass bushings
650X200 mm
| Supply -Basic | Sq Mtrs | 1 | 1416 | 121.455
| Accessories | Sq Mtrs | 1 | 283.2 | 24.291
| Unloading & Shifting charge | Sq Mtrs | 1 | 141.6 | 12.1455
| Sub Total |  |  | 1840.8 | 157.8915
| Over Head Profit @ 13 % |  | 1 | 239.304 | 20.5259
| Margin @ 10% |  | 1 | 184.08 | 15.7892
| Total |  |  | 2264.184 | 194.2065
Installation & Testing Commissioning
| labour rate with Tools -Fitter +Helper | Hours | 1 | 339.6276 | 29.16
| Commissioning charge | No. |  | 100 | 11.44
| Sub Total |  |  | 439.6276 | 40.6
| Over Head Profit @ 13 % |  | 1 | 57.1516 | 5.278
| Margin @ 10% |  | 1 | 43.9628 | 4.06
| Total |  |  | 540.7419 | 49.938
| Supply +Installation Total |  |  | 2804.9259 | 244.1445
400 X 150 mm
| Supply -Basic | Sq Mtrs | 1 | 578 | 49.575
| Accessories | Sq Mtrs | 1 | 115.6 | 9.915
| Unloading & Shifting charge | Sq Mtrs | 1 | 57.8 | 4.9575
| Sub Total |  |  | 751.4 | 64.4475
| Over Head Profit @ 13 % |  | 1 | 97.682 | 8.3782
| Margin @ 10% |  | 1 | 75.14 | 6.4447
| Total |  |  | 924.222 | 79.2704
Installation & Testing Commissioning
| labour rate with Tools -Fitter +Helper | Hours | 1 | 138.6333 | 11.8906
| Commissioning charge | No. |  | 100 | 11.44
| Sub Total |  |  | 238.6333 | 23.3306
| Over Head Profit @ 13 % |  | 1 | 31.0223 | 3.033
| Margin @ 10% |  | 1 | 23.8633 | 2.3331
| Total |  |  | 293.519 | 28.6966
| Supply +Installation Total |  |  | 1217.741 | 107.967
350 X100 mm
| Supply -Basic | Sq Mtrs | 1 | 578 | 49.575
| Accessories | Sq Mtrs | 1 | 115.6 | 9.915
| Unloading & Shifting charge | Sq Mtrs | 1 | 57.8 | 4.9575
| Sub Total |  |  | 751.4 | 64.4475
| Over Head Profit @ 13 % |  | 1 | 97.682 | 8.3782
| Margin @ 10% |  | 1 | 75.14 | 6.4447
| Total |  |  | 924.222 | 79.2704
Installation & Testing Commissioning
| labour rate with Tools -Fitter +Helper | Hours | 1 | 110.9066 | 9.5125
| Commissioning charge | No. |  | 100 | 11.44
| Sub Total |  |  | 210.9066 | 20.9525
| Over Head Profit @ 13 % |  | 1 | 27.4179 | 2.7238
| Margin @ 10% |  | 1 | 21.0907 | 2.0952
| Total |  |  | 259.4152 | 25.7715
| Supply +Installation Total |  |  | 1183.6372 | 105.0419
1.3 | Supply ,Installation & Testing of HEPA FILTER H14- ( 450 X450 mm size) | No.s | 8
| Supply -Basic | Sq Mtrs | 1 | 28856 | 1650
| Accessories | Sq Mtrs | 1 | 5771.2 | 330
| Unloading & Shifting charge | Sq Mtrs | 1 | 2885.6 | 165
| Sub Total |  |  | 37512.8 | 2145
| Over Head Profit @ 13 % |  | 1 | 4876.664 | 278.85
| Margin @ 10% |  | 1 | 3751.28 | 214.5
| Total |  |  | 46140.744 | 2638.35
Installation & Testing Commissioning
| labour rate with Tools -Fitter +Helper | Hours | 1 | 5536.8893 | 316.602
| Commissioning charge | No. |  | 50 | 5.72
| Sub Total |  |  | 5586.8893 | 322.322
| Over Head Profit @ 13 % |  | 1 | 726.2956 | 41.9019
| Margin @ 10% |  | 1 | 558.6889 | 32.2322
| Total |  |  | 6871.8738 | 396.4561
| Supply +Installation Total |  |  | 53012.6178 | 3034.8061

## HVAC BOQ-1
SI. NO | DISCRIPTION OF ITEM | UOM | QTY | price | sum
1 | EQUIPMENTS |  |  |  | 0
1.1 | VRF Outdoor Units |  |  |  | 0
| SITC of Digital / invert type VRF ODU. VRF Modular outdoor condensing units shall be (Heat pump type) equipped with highly efficient multiple scroll compressor with atleast one inverter compressor. All compressors being inverter type are also acceptable. Special acryl pre-quoted fin type heat exchanger. Super wiring system to integrate the control wiring between indoor units and the outdoor units and the transmission wiring to central remote controller into one common wiring. Unit cooling capacity shall be based on ambient temperature of 35 deg C, shall include low ambient controls and accessories operational to -10 deg.F and shall possess refrigerant R410A and Minimum SEER of 15. The unit shall be suitable to work on 400 V +/-10%, 3 Phase, 50 Hz AC power supply. Quoted price shall be inclusive of suitable ELCB for power provision. Capacities stated are tentative. Supplier shall verify the equipment schedule and propose the capacity to suit the design Note: The above mentioned outdoor units shall be provided with anti corrosion treatment (preferably from factory). The quoted price shall be inclusive of same. |  |  |  | 0
1.1.1 | System-02 VRF Outdoor Unit 12 HP-terrace floor | Nos | 1 |  | 0
1.1.2 | System-01 VRF Outdoor Unit 26 HP (18+10)-terrace floor | Nos | 1 |  | 0
1.2 | Customized VRF Indoor Units |  |  |  | 0
| Air Handling Unit |  |  |  | 0
| SITC of Double Skin Vertical / Horizontal type Floor Mounted type Air handling units with 46+/-2mm thick puff Insulated 48kg / m3 density TF quality sandwich panel and it shall be complete with double skin construction with thermal breaks assembled on extruded aluminium frame work as per the detailed specification given in AHU schedule oil section with six rows deep DX cooling coil of copper tube & aluminium fin construction, squirrel cage induction motor, DIDW Backward curve Direct Driven fan,thermal break and vibration isolators as per the AHU specifications. Coil size shall be selected for a maximum face velocity of 500 feet/minute and static pressure shall be as indicated. The motor selected shall be energy efficient having efficiency (Class I) at full load ranging between 82.5% to 92% in accordance with motor rating as per specification.Motor shall be suitable for 415±10% volts, 50 cycles, 3 phase AC supply. Units shall be complete with opposed blade volume control dampers at supply and return air connections.Duct flexible connector (fire proof) shall be provided at out lets and return connections of AHU. AHU shall be with 3 stage (Prefilter, final filter and HEPA filter) filtration with UV lamp next to filter. Exhaust shall be exhausted through a HEPA filter and UV lamp. Inner skin shall be Aluminium. (For Laborotory) |  |  |  | 0
| AHU SA Flow ESP RA Flow ESP No. of Coil load EA Capacity |  |  |  | 0
| No. (L/S) (mm WG) (L/s) (mm WG) Rows kw (L/s) |  |  |  | 0
1.2.1 | GF-AHU-01 3100 25 4100 - 6 45 clg/ 59 htg 720 | No | 1 |  | 0
1.3 | VRF Ductable unit |  |  |  | 0
| SITC of Ductable Indoor (Heating and cooling), shall be with EC motors ,air purifying filters of non-woven type suitable for long life replacement. Refnet piping system to integrate indoor and outdoor units. Standard Accessories – operation manual, installation manual, paper pattern for installation, drain hose, clamp metal, insulation for fittings, sealing pads, dampers, screws, washers etc.Slotted angle iron tray to house refrigeration piping and electrical and control cabling complete with clamps, screws, washers etc. Separate condensate water tray shall be provided for all units with high level alarm. Units shall be capable of fresh air intake as mentioned in the specifications. |  |  |  | 0
1.3.1 | GF-IDU-01-01A- 9.7 kw Clg/5.0 Htg, 15 mm WG | Nos | 1 |  | 0
1.3.2 | GF-IDU-03- 5.4 kw Clg/ 5.4 kw Htg 5 mm WG | Nos | 2 |  | 0
1.3.3 | GF-IDU-05- 4.0 kw Clg/ 4.0 kw Htg mm WG | Nos | 1 |  | 0
1.3.4 | GF-IDU-06- 1.8 kw Clg/ 0.8 kw Htg 5 mm WG | Nos | 1 |  | 0
1.4 | VRF Cassette unit |  |  |  | 0
| SITC of following minimum capacity 4-way flow VRV /VRF Cassette type Indoor ceiling mounted unit (Heating and cooling) equipped with washable synthetic media pre-filter, fan section with low noise fan /dynamically balanced blower, multi-speed motor, coil section with DX copper coil, electronic expansion valve, outer cabinet, drain pump, necessary supports, cordless remote control, drain pan, necessary accessories etc., suitable for operation on 230 V ± 10 %, 50 Hz, single phase AC supply complete as required. |  |  |  | 0
1.4.1 | GF-IDU-01-01B/1C- 2.7 kw Clg/ 1.5kw Htg | Nos | 2 |  | 0
1.4.2 | GF-IDU-02- 6.1 kw Clg/ 5.0 kw Htg | Nos | 1 |  | 0
1.4.3 | GF-IDU-07- 2.3 kw Clg/ 2.3 kw Htg | Nos | 1 |  | 0
1.4.4 | GF-IDU-08- 1.0 kw Clg/ 0.5 kw Htg | Nos | 1 |  | 0
1.4.5 | GF-IDU-09- 1.1 kw Clg/ 0.6 kw Htg | Nos | 1 |  | 0
1.4.6 | GF-IDU-10- 0.1 kw Clg/ 0.6 kw Htg | Nos | 1 |  | 0
1.4.7 | GF-IDU-11- 0.1 kw Clg/ 0.6 kw Htg | Nos | 1 |  | 0
1.4.8 | IF-IDU-01- 3.6 kw Clg/ 3.0 kw Htg | Nos | 1 |  | 0
1.4.9 | IF-IDU-02- 2.8 kw Clg/ 1.8 kw Htg | Nos | 1 |  | 0
1.4.10 | IF-IDU-03- 2.8 kw Clg/ 136 kw Htg | Nos | 1 |  | 0
1.4.11 | IF-IDU-04- 2.6 kw Clg/ 1.4 kw Htg | Nos | 1 |  | 0
1.4.12 | IF-IDU-05- 3.9 kw Clg/ 2.2 kw Htg | Nos | 1 |  | 0
1.4.13 | IF-IDU-06A & 06B- 2.3 kw Clg/ 1.4 kw Htg | Nos | 2 |  | 0
1.4.14 | IF-IDU-07A & 07B- 3.4 kw Clg/ 1.3 kw Htg | Nos | 2 |  | 0
1.4.15 | IF-IDU-08- 3.9 kw Clg/ 2.3 kw Htg | Nos | 1 |  | 0
1.4.16 | IF-IDU-09- 4.7 kw Clg/ 6.0 kw Htg | Nos | 1 |  | 0
1.4.17 | IF-IDU-10- 1.5 kw Clg/ 1.4 kw Htg | Nos | 1 |  | 0
1.5 | Dx-Split Hi-Wall Unit |  |  |  | 0
| SITC of High efficiency (Minimum SEER-15) DX-Split Hi-wall unit (Cooling only), shall be with Standard Accessories – operation manual, installation manual, paper pattern for installation, suction and liquid line with insulation, drain hose, clamp metal, insulation for fittings, sealing pads, screws, washers etc.Slotted angle iron tray to house refrigeration piping and electrical and control cabling complete with clamps, screws, washers etc. suitable for operation on 230 V ± 10 %, 50 Hz, single phase AC supply complete as required. Unit cooling capacity shall be based on ambient temperature of 35 deg C |  |  |  | 0
1.5.1 | 1F-IDU-11/CU-11- 7.8 kw- For Electrical room | Nos | 1 |  | 0
| SITC of High efficiency (Minimum SEER-15) DX-Split ductable unit (Cooling & Heeting ), shall be with Standard Accessories – operation manual, installation manual, paper pattern for installation, suction and liquid line with insulation, drain hose, clamp metal, insulation for fittings, sealing pads, screws, washers etc.Slotted angle iron tray to house refrigeration piping and electrical and control cabling complete with clamps, screws, washers etc. suitable for operation on 230 V ± 10 %, 50 Hz, single phase AC supply complete as required. Unit cooling capacity shall be based on ambient temperature of 35 deg C |  |  |  | 0
1.5.2 | GF-IDU-04/CU-04- 15.5 kW Clg/14.2 Htg | Nos | 1 |  | 0
0
1.6 | Electric Unit Heater |  |  |  | 0
| SITC of Electric Unit heaters with electric and control cable clamp metal screw, washer etc. Shall be suitable for operation on 230 V ± 10 %, 50 Hz, single phase AC supply complete as required. Shall be wall mounted type. |  |  |  | 0
1.6.1 | GF-UH-01/02-1.3 Kw | Nos | 2 |  | 0
1.7 | Fans Suitable for operation on 230 V ± 10 %, 50 Hz, single phase AC supply |  |  |  | 0
1.7.1 | Supply, Installation, Testing & Commissioning of Roof top centrifugal exhaust fan, with the capacity of 311 L/s, 500 Pa -GF-EF-01 | Nos | 1 |  | 0
1.7.2 | Supply, Installation, Testing & Commissioning of IN-LINE DIRECT DRIVEN CABINET EXHAUST FAN, with the capacity of 88 L/s, 70 Pa -GF-EF-02 & 03 | Nos | 2 |  | 0
1.7.3 | Supply, Installation, Testing & Commissioning of IN-LINE CENTRIFUGAL CIRCULAR EXHAUST FAN, with the capacity of 160 L/s, 50 Pa - GF-EF-05 | Nos | 1 |  | 0
1.7.4 | Supply, Installation, Testing & Commissioning of CEILING MOUNTED EXHAUST FAN, with the capacity of 56 L/s, 50 Pa-GF-EF-04 | Nos | 1 |  | 0
1.7.5 | Supply, Installation, Testing & Commissioning of IN-LINE CENTRIFUGAL CIRCULAR EXHAUST FAN, with the capacity of 50 L/s, 50 Pa -GF-EF-06 | Nos | 1 |  | 0
1.7.6 | Supply, Installation, Testing & Commissioning of IN-LINE CENTRIFUGAL CIRCULAR EXHAUST FAN, with the capacity of 125 L/s, 50 Pa -GF-EF-07 | Nos | 1 |  | 0
1.7.7 | Supply, Installation, Testing & Commissioning of IN-LINE CENTRIFUGAL CIRCULAR EXHAUST FAN, with the capacity of 75 L/s, 130 Pa 1F-EF-02 | Nos | 1 |  | 0
1.7.8 | Supply, Installation, Testing & Commissioning of IN-LINE DIRECT DRIVEN CABINET EXHAUST FAN, with the capacity of 155 L/s, 100 Pa - GF-EF-08 | Nos | 1 |  | 0
1.7.9 | Supply, Installation, Testing & Commissioning of Roof top centrifugal exhaust fan, with the capacity of 306 L/s, 100 Pa - GF-EF-09 | Nos | 1 |  | 0
1.7.10 | Supply, Installation, Testing & Commissioning of Roof top centrifugal exhaust fan, with the capacity of 128 L/s, 100 Pa - GF-EF-10 | Nos | 1 |  | 0
1.7.11 | Supply, Installation, Testing & Commissioning of Roof top centrifugal exhaust fan, with the capacity of 278 L/s, 100 Pa -GF-EF-11 | Nos | 1 |  | 0
1.7.12 | Supply, Installation, Testing & Commissioning of Roof top centrifugal exhaust fan, with the capacity of 150 L/s, 100 Pa --GF-EF-12 | Nos | 1 |  | 0
1.7.13 | Supply, Installation, Testing & Commissioning of CEILING MOUNTED EXHAUST FAN, with the capacity of 50 L/s, 130 Pa - 1F-EF-01 | Nos | 1 |  | 0
1.7.14 | Supply, Installation, Testing & Commissioning of CEILING MOUNTED TYPE EXHAUST FAN, with the capacity of 36 L/s, 50 Pa -1F-EF-03 | Nos | 1 |  | 0
1.8 | Variable Air Volume Units |  |  |  | 0
| SITC of VAV unit for supply air for rectangular ducts with thermostat and control. Vav Casing and damper blade made of galvanized sheet steel with proper seal and polyurethane plain bearings. Sensor tubes should be aluminium, maintenance free damper blade with minimum leakage rate.Actuator suitable for AC 24V 50 Hz and rated for dust pressure up to 50mm water gauge. As per detailed schedule | Nos | 8 |  | 0
1.9.1 | Air Curtain |  |  |  | 0
| SITC of ambient air curtain suitable for entrace doors |  |  |  | 0
1.9.1.1 | 1 Meter Legth- Air curtain 02 | Nos | 1 |  | 0
1.9.1.2 | 2.1 Meter Length -Air curtain 01 | Nos | 2 |  | 0
1.9.2 | RECUPERATOR |  |  |  | 0
| SITC High efficiency single zone/multizone of recuperator with EC fans suitable for ceiling instation. Efficicancy shall be above 90% |  |  |  | 0
1.9.2.1 | 260 L/s | Nos | 2 |  | 0
1.9.2.2 | 100 L/s | Nos | 1 |  | 0
2 | PIPING AND ITS ACCESSORIES |  |  |  | 0
2.1 | REFRIGERANT PIPING |  |  |  | 0
| Supply,installation,testing, commissioning of of high pressure Gas/ Liquid Copper Piping with nitrile rubber class 'O' insulation of suitable thick round closed cell elastomeric insulation finished with 7mils woven fiber glass cloth covering adhered between two coats of fungicidal protective coating and insulation shall have antimicrobial properties, suction filters for gas line, filter drier & sight glass for liquid line as per specification for each indoor machines & outdoor units including chasing, drilling, concealing and making good the same on walls etc of following specifications as per site conditions and with required pipe fittings and accessories like Bends, Tees, reducers, supports, clamps, refnets etc.Complete in all respects as per technical specifications. NOTE: The contractor shall ensure that all refrigerant pipe sizes required as per the design of the equipment shall be considered in the line items underneath, even if the refrigerant pipe size is not mentioned in following line items.Both refrigerant suction and liquid line shall be insulated. External Refrigerant piping shall be laid on GI covered cable trays. Piping inside occupied spaces shall be supported using GI ladder type cable trays. |  |  |  | 0
2.1.1 | Hard Copper Pipe 18Guage with 19mm thick Insulation ( 53.9 MM) | Rmt
2.1.2 | Hard Copper Pipe 18Guage with 19mm thick Insulation ( 44.45MM) | Rmt
2.1.3 | Hard Copper Pipe 18Guage with 19mm thick Insulation ( 41.2MM) | Rmt
2.1.4 | Hard Copper Pipe 18Guage with 19mm thick Insulation ( 34.9MM) | Rmt
2.1.5 | Hard Copper Pipe 18Guage with 19mm thick Insulation ( 31.8MM) | Rmt | 32 |  | 0
2.1.6 | Hard Copper Pipe 18Guage with 19mm thick Insulation ( 28.6MM) | Rmt | 14 |  | 0
2.1.7 | Hard Copper Pipe 18Guage with 13mm thick Insulation ( 25.4 MM) | Rmt | 24 |  | 0
2.1.8 | Hard Copper Pipe 18Guage with 13mm thick Insulation ( 22.2MM) | Rmt | 34 |  | 0
2.1.9 | Hard Copper Pipe 18Guage with 13mm thick Insulation ( 19.05MM) | Rmt | 45 |  | 0
2.1.10 | Hard Copper Pipe 18Guage with 13mm thick Insulation ( 15.9MM) | Rmt | 55 |  | 0
2.1.11 | Hard Copper Pipe 18Guage with 13mm thick Insulation ( 12.7MM) | Rmt | 152 |  | 0
2.1.12 | Hard Copper Pipe 18Guage with 13mm thick Insulation ( 9.53MM) | Rmt | 39 |  | 0
2.1.13 | Hard Copper Pipe 18Guage with 13mm thick Insulation ( 6.35MM) | Rmt | 53 |  | 0
2.2 | Refnet Joints and Headers |  |  |  | 0
| Shall be used for interconnection between indoor and outdoor units. Shall be selected by the supplier depending on the machine configuration. Number of joints shall be minimized and optimized to suit system performance.Isulation shall be done. |  |  |  | 0
2.2.1 | Outdoor refnet joints | Nos | 1 |  | 0
2.2.2 | Indoor refnet joints | Nos | 24 |  | 0
3 | DUCTING AND ITS ACCESSORIES |  |  |  | 0
3.1 | Duct work |  |  |  | 0
3.1.1 | Factory Fabricated |  |  |  | 0
| Supply, Installation, Testing & Commissioning of factory fabricated ductwork, Installation and Testing of galvanized sheet metal ducts including elbows, turning vanes, fire retardant gaskets, slip on flanges, GI fully threaded rods, GI supports/hangers etc. in accordance with the approved shop drawings and specifications. The ducts shall be fabricated and installed in line with SMACNA standards. |  |  |  | 0
3.1.1.1 | 24 G | Sq mtr | 1000 |  | 0
3.1.1.2 | 22 G | Sq mtr |  |  | 0
3.1.1.3 | 20 G | Sq mtr |  |  | 0
3.1.1.4 | 18 G | Sq mtr |  |  | 0
3.1.2 | Conventional site fabricated ducts using Lock Forming Machines. |  |  |  | 0
| Supply, Fabrication, Installation and Testing of sheet metal ducts in accordance with the approved shop drawings and specifications. Ducts shall be fabricated using lock forming machine. | LOT |  |  | 0
3.2 | Flexible duct joints |  |  |  | 0
| Supply, Installation, Testing & Commissioning of 125mm deep Antivibration Flexible Joints made out of imported fire retardant fabric with extruded aluminium frame/ flange on both sides of approved make. |  |  |  | 0
| 100 MM | Rmt | 25 |  | 0
0
4 | GRILLES,DIFFUSERS,LOUVERS |  |  |  | 0
4.1 | Louvers |  |  |  | 0
| Supply, installation, testing and balancing of Factory made fresh air louvers with bird screen as per approved shop drawings. Shall be of approved colour & shade. As per detailed schedule | Sq.mtr | 2 |  | 0
4.5 | Door Louvers |  |  |  | 0
4.5.1 | Supply, Installation & Testing of extruded aluminium powder coated air transfer grilles/ louvers to be provided at toilets doors & above kitchen doors, as per approved shop drawings and specifications. | Sq.mtr
5 | INSULATION |  |  |  | 0
5.1 | Thermal Insulation |  |  |  | 0
| Supply and Application of external thermal insulation of ducting using closed cell elastomeric insulation with adhesive, longitudinal & transverse joints sealed with adhesive as per specifications. Quoted price shall be inclusive of adhesive and UV/ Mechanical Protection using resistant paint & Glass cloth/CSM |  |  |  | 0
| 19 mm , Nitrile rubber | Sq.mtr | 600 |  | 0
5.2 | Acoustic insulation |  |  |  | 0
| SITC of acoustic insulation following thick open cell nitrile rubber foam and properties of classO ,anti microbail,density of 140-180kg/m3 and applying the same on duct with glue. |  |  |  | 0
| 15 mm , Nitrile rubber | Sq.mtr | 120 |  | 0
6 | CONTROLS |  |  |  | 0
6.1 | Variable Frequency Drives |  |  |  | 0
| Supply Installation, Testing and Commissioning of variable frequency drives for Air Handling Units Supply and return fans. Variable frequency drives shall be provided with necessary sensors and controllers complete with control wiring in all respect as required and as per the specifications. VFDs shall be provided with necessary bypass arrangement with existing electrical starter panels and IP-55 enclosure. The drives shall be suitable for the following motor rating: (Motor rating has to be checked and confirmed as per installed capacities) |  |  |  | 0
| 5 Kw -For AHU Supply fan | Nos | 1 |  | 0
6.2 | Centralized master controller |  |  |  | 0
| Supply, Installation, Testing and Commissioning of main centralized controller to hook up indoor units . Controller shall however be suitable for 40 groups of indoor units (including customized AHUs). The quoted price shall be inclusive of necessary BMS card & integrator, controllers & accessories required for BMS connectivity with Modbus/BACnet protocol. | Nos | 1 |  | 0
6.3 | DP sensors | Nos | 7 |  | 0
6.4 | Pressure sensors | Nos | 5 |  | 0
6.5 | Control wiring |  |  |  | 0
6.5.1 | Indoor to thermostat control cabling with PVC sheathed CU cable of 2C X 1.5SQMM through PVC conduits (If units are remote controlling type, it cannot be considered) | Rmt | 210 |  | 0
6.5.2 | Indoor to outdoor unit control cabling with PVC sheathed CU cable of 3C X 0.75 SQMM through PVC conduits. | Rmt | 224 |  | 0
6.6 | Power Cabling |  |  |  | 0
| Supply, laying, affecting connections & Testing of the following sizes of 1.1 KV armoured PVC insulated aluminium/ copper conductor cables. Cables shall be inclusive conductor cables. Cables shall be inclusive of all clamps, saddles, screws, cable identification tags, cable terminal joints including terminal lugs, insulating tapes, MS conduit, affecting terminal connections to the equipment as per the specifications and as required. | Rmt | 300 |  | 0
6.6.1 | 4C x 6 Sqmm cable (Copper) | LOT |  |  | 0
6.6.2 | 4C x 4 Sqmm cable (Copper) | LOT |  |  | 0
6.6.3 | 4C x 2.5 Sqmm cable (Copper) | LOT |  |  | 0
6.6.4 | 4C x 10 Sqmm cable (Copper) | LOT |  |  | 0
6.7 | CONDENSATE DRAIN PIPE |  |  |  | 0
| Providing and fixing in position the following GI medium class pipes for condensate drain cut to required lengths and installed with all screwed joints and providing & fixing in position the necessary elbows, tees & reducers with 25mm nitrile rubber insulation |  |  |  | 0
6.7.1 | 25 mm dia PVC drain pipe | Rmt | 129.3 |  | 0
6.7.2 | 32 mm dia PVC drain pipe | Rmt | 27.8 |  | 0
6.7.3 | 40 mm dia PVC drain pipe | Rmt | 19 |  | 0
0

## VRF-ODU
VRF CONDENSING UNIT
Sl.No | SYSTEM REF | UNIT TYPE | AREA SERVED | TOTAL COOLING CAP |  |  | TOTAL HEATING CAP |  | SYSTEM CONFIGURATION | POWER CONSUPTION | POWER TYPE | LOCATION OF UNIT
- | - | - | - | kW | MBH | TR | kW | MBH | HP | kW |  | -
1 | SYSTEM-01 | Heat pump (Heating and cooling) | Ground Floor | 78.93 | 269.0795 | 22.4233 | 87.7 | 298.9773 | 28 HP (12HP+16HP Nos) | 18.52 | 3-Phase 400 V, 50 HZ | Roof
2 | SYSTEM-02 | Heat pump (Heating and cooling) | First Floor | 33.21 | 113.2159 | 9.4347 | 25.6 | 87.2727 | 12 HP (12HPX1No) | 10.98 |  | Roof

## DX-SPLIT
INDOOR UNIT SCHEDULE
SL NO | TYPE OF AC | Area Served | AHU TAG | Supply Fan |  | Qty | IDU SCHEDULE | [9 empty] | Power consuption |  | Remark
[7 empty] | COOLING COIL DATA (DESIGN PARAMTER) |  |  |  | HEATING COIL DATA (DESIGN PARAMTER) |  |  | SELECTION | [5 empty] | Cooling TR | Heating TR
|  |  |  | Air Flow Rate | External Static ESP |  | Total Coil load | Sensible coil load | Entering Air DB/WB | Leaving Air DB/WB | Total Coil load | Entering Air DB | Leaving Air DB | Total Capacity | Air flow rate | Coil Type and row coil
|  |  |  | LPS | Pa |  | kW | kW | °C | °C | kW | °C | °C | TR | CFM |  | Type | W atts
FIRST FLOOR
1 | Hi-Wall | Electrical Room | 1F-IDU-11/CU-11 | 583 | - | 1 | 7.8 | 7.8 | 24.1 / 16.5 | 13.0 / 12.3 | - | - | - | - | - | - | 1-phase, 230V 50Hz | 2200 | Cooling only | 2.2159 | -
2 | Floor standing ductable | Storage | GF-IDU-04/CU-04 | 1438 | 75 | 1 | 15.5 | 14.5 | 22.6 / 17.2 | 14.5 / 14.0 | 14.2 | 16.8 | 24.7 | - | - | - | 1-phase, 230V 50Hz | 5284.0909 | Heat Pump
Notes:
1.Given are Nominal capacities, Actual selection shall be done as per maximum ambient condition.
2.Power consumption given are approximate, actual power consuption shall be consider as per equipment technical data sheet

## VRF_IDU
| Proj. | Medtrader Lab LLC
| Doc. | Indoor unit schedule
| Prepared by | Aneesh U
| Date: | 03.03.2022
INDOOR UNIT SCHEDULE
SL NO | TYPE OF AC | Area Served | AHU TAG | Supply Fan |  | Return Fan |  | Exhaust Air Flow Rate | Fresh Air Flow Rate | Qty | From supplier's catalogue | IDU SCHEDULE | [9 empty] | HEPA filter | Fine filter | Prefilter | Mixing box | Return air duct required/not required | UV Lamp | Humidifier | Power consumption |  | Remark
[12 empty] | COOLING COIL DATA (DESIGN PARAMTER) |  |  |  | HEATING COIL DATA (DESIGN PARAMTER) |  |  | SELECTION | [13 empty] | Cooling TR | Heating TR
|  |  |  | Air Flow Rate | External Static ESP | Air Flow Rate | External Static ESP |  |  |  |  | Total Coil load | Sensible coil load | Entering Air DB/WB | Leaving Air DB/WB | Total Capacity | Entering Air DB | Leaving Air DB | Total Capacity | Air flow rate | Coil Type and row coil
|  |  |  | LPS | Pa | LPS | Pa | CFM | CFM |  | kw | kW | kW | °C | °C | kW | °C | °C | TR | CFM |  | 0.3 Microns | 5 Microns | 10 microns |  |  |  | Lb/hr | Type | W atts
GROUND FLOOR
1 | FLM | Bacteriology room /working area | GF-AHU-01 | 3000 | 400 | 2900 | - | 720 | 1200 | 1 |  | 45 | 42.6 | 25.9 / 19.1 | 16.3 / 15.7 | 59 | 13.5 | 26.7 | - | - | - | YES | YES | YES | YES | YES | YES | _ | 3-Phase 400 V, 50/60 Hz | 5000 | *Suit for outside installation *With VFD for supply fan *Final capacity as per vendor selection *Required HEPA filter with UV lamp at exhaust side also |  | 12.7841 | 16.7614
2 |  | Bacteriology preparation room
3 |  | Arch Zone 23-27 +Aliquoting area
4 |  | Zone-03
5 |  | Biochemistry/Microscope+Faeces Microscopy+Citology
6 |  | Emergency room
7 |  | BCC children
8 |  | BCC adult-2
9 |  | BCC adult-1
10 |  | Male specimen collection room
11 |  | Female specimen collection room
12 |  | Zone-01
13 |  | WD - 005
14 |  | Extraction room
15 |  | Pre- Pcr Master mix area
16 |  | pcr analyzer/diagnosis
Reception-Labelling-Dispatching
17 |  | prebox + pcr warehouse
18 | CSU | Patient Reception | GF-IDU-01A | 615.7262 | 150 | - | - | - | - | 1 | 14 | 9.68 | 8 | - | - | 6 | - | - | - | - | - | - | - | - | - | - | - | - | 1-phase, 220-240V,50Hz | 724 | Bottom return |  | 2.75 | 1.7045
19 | CASSETTE |  | GF-IDU-01B/01C | 191.6369 | - | - | - | - | - | 2 | 2.8 | 2.7 | 1.5 | - | - | 1.55 | - | - | - | - | - | - | - | - | - | - | - | - | 1-phase, 220-240V,50Hz | 57 |  |  | 1.5341 | 0.88068
20 | CSU | Quality officer room | GF-IDU-03 | 250 | 30 | - | - | - | - | 1 | 8 | 5.4 | 4 | - | - | 5.4 | - | - | - | - | - | - | - | - | - | - | - | - | 1-phase, 220-240V,50Hz | 198 |  |  | 1.5341 | 1.5341
21 |  | Lab manager room | [19 empty] | - | - | - | - | - | - | -
23 | CSU | Living room | GF-IDU-05 | 139 | 30 | - | - | - | - | 1 | 4.5 | 4 | 3.1 | - | - | 4 | - | - | - | - | - | - | - | - | - | - | - | - | 1-phase, 220-240V,50Hz | 98 |  |  | 1.1364 | 1.1364
24 |  | Drivers room | [19 empty] | - | - | - | - | - | - | -
26 | CSU | Autoclave sterilization room+waste room | GF-IDU-06 | 177 | 30 | - | - | - | - | 1 | 7.1 | 1.8 | 1.6 | - | - | 0.8 | - | - | - | - | - | - | - | - | - | - | - | - | 1-phase, 220-240V,50Hz | 140 |  |  | 0.51136 | 0.22727
27 | CASSETTE | kitchen | GF-IDU-02 | 350 | - | - | - | - | - | 1 |  | 6.1 | 5.4 | - | - | 5 | - | - | - | - | - | - | - | - | - | - | - | - | 1-phase, 220-240V,50Hz | 140 |  |  | 1.733 | 1.4205
7 | CASSETTE | BCC children | GF-IDU-07 | 235 | - | - | - | - | - | 1 | kW: 3.2; kW: 3.1; °C: -; °C: -; kW: 2.3 | [8 empty] | 1-phase, 220-240V,50Hz | 108 |  |  | 0.90909 | 0.65341
8 | CASSETTE | BCC adult-2 | GF-IDU-08 | 53 | - | - | - | - | - | 1 | kW: 1; kW: 0.9; °C: -; °C: -; kW: 0.5 | [8 empty] | 1-phase, 220-240V,50Hz | 57 |  |  | 0.28409 | 0.14205
9 | CASSETTE | BCC adult-1 | GF-IDU-09 | 65 | - | - | - | - | - | 1 | kW: 1.1; kW: 0.9; °C: -; °C: -; kW: 0.6 | [8 empty] | 1-phase, 220-240V,50Hz | 57 |  |  | 0.3125 | 0.17045
10 | CASSETTE | Male specimen collection room | GF-IDU-10 | 50 | - | - | - | - | - | 1 | kW: 0.9; kW: 0.7; °C: -; °C: -; kW: 0.5 | [8 empty] | 1-phase, 220-240V,50Hz | 57 |  |  | 0.25568 | 0.14205
11 | CASSETTE | Female specimen collection room | GF-IDU-11 | 50 | - | - | - | - | - | 1 | kW: 0.9; kW: 0.7; °C: -; °C: -; kW: 0.5 | [8 empty] | 1-phase, 220-240V,50Hz | 57 |  |  | 0.25568 | 0.14205
FIRST FLOOR | [32 empty] | 24 | 24.9148
1 | CASSETTE | Cabinet N2 | IF-IDU-01 | 264 | - | - | - | - | - | 1 | 5.6 | 3.6 | 3.5 |  |  | 3 |  |  | - | - | - | - | - | - | - | - | - | - | 1-phase, 220-240V,50Hz | 65 |  |  | 1.0227 | 0.85227
2 | CASSETTE | Cabinet N1 | IF-IDU-02 | 192 | - | - | - | - | - | 1 | 2.8 | 2.8 | 2.6 |  |  | 1.8 |  |  | - | - | - | - | - | - | - | - | - | - | 1-phase, 220-240V,50Hz | 65 |  |  | 0.79545 | 0.51136
3 | CASSETTE | Office N1 | IF-IDU-03 | 165 | - | - | - | - | - | 1 | 2.8 | 2.5 | 2.2 |  |  | 1.3 |  |  | - | - | - | - | - | - | - | - | - | - | 1-phase, 220-240V,50Hz | 65 |  |  | 0.71023 | 0.36932
4 | CASSETTE | Office N2 | IF-IDU-04 | 170 | - | - | - | - | - | 1 | 2.8 | 2.6 | 2.3 |  |  | 1.4 |  |  | - | - | - | - | - | - | - | - | - | - | 1-phase, 220-240V,50Hz | 65 |  |  | 0.73864 | 0.39773
5 | CASSETTE | Office N3 | IF-IDU-05 | 258 | - | - | - | - | - | 1 | 14 | 3.9 | 3.5 |  |  | 2.2 |  |  | - | - | - | - | - | - | - | - | - | - | 1-phase, 220-240V,50Hz | 75 |  |  | 1.108 | 0.625
6 | CASSETTE | Office N4 | IF-IDU-06A & 06B | 151.5 | - | - | - | - | - | 2 | 2.8 | 2.3 | 2.05 |  |  | 1.4 |  |  | - | - | - | - | - | - | - | - | - | - | 1-phase, 220-240V,50Hz | 65 |  |  | 1.3068 | 0.79545
10 | CASSETTE | Kitchen | IF-IDU-07A & 07B | 227 | - |  |  |  |  | 2 | 7.1 | 3.4 | 3.1 |  |  | 1.7 |  |  | - | - | - | - | - | - | - | - | - | - | 1-phase, 220-240V,50Hz | 65 |  |  | 1.9318 | 0.96591
13 | CASSETTE | Meeting Room | IF-IDU-08 | 221 | - |  |  |  |  | 1 | kw: 3.6; kW: 3.9; kW: 3.1; kW: 2.3 | [8 empty] | 1-phase, 220-240V,50Hz | 75 |  |  | 1.108 | 0.65341
14 | CASSETTE | Reception and corridor | IF-IDU-09 | 333 | - |  |  |  |  | 1 | kw: 3.6; kW: 4.7; kW: 4.4; kW: 6 | [8 empty] | 1-phase, 220-240V,50Hz | 65 |  |  | 1.3352 | 1.7045
15 | CASSETTE | Private room | IF-IDU-10 | 91 | - |  |  |  |  | 1 | kw: 2.2; kW: 1.5; kW: 1.2; kW: 1.4 | [8 empty] | 1-phase, 220-240V,50Hz | 65 |  |  | 0.42614 | 0.39773
[33 empty] | 10.483 | 7.2727
|  | Notes: | [28 empty] | Description | GROUND FLOOR (CU-01) | FIRST FLOOR (CU-02)
|  | 1.Given are Nominal capacities, Actual selection shall be done as per maximum ambient condition. | [28 empty] | Total coil load (TR) | 24.9148 | 10.483
|  | 2.AHUs serving to Lab area shall be with 3 stage filtration (Prefilter, Final filter and HEPA filter) and shall be with inbult UV-Lamp | [28 empty] | Hcoil load after 10% diversity (TR) | 22.4233 | 9.4347
|  | 3.Power consumption given are approximate, actual power consuption shall be consider as per equipment technical data sheet | [28 empty] | ODU Capacity in HP | 28.0291 | 11.7933
[31 empty] | Power consumption (kW) | 17.2 | 11
Note.
Given is nominal capacity, selection shall be done based on actual capacity at maximum ambient temperature
33.21

## RECUPERATOR
RECUPERATOR DETAILS
FLOOR SERVING | TAG | Qty | AREA | FLOW RATE L/s | STATIC PRESSURE (Pa) | POWER TYPE | ELECTRICAL POWER (W) | MAKE | MODEL
GROUND FLOOR | REC-1 | 1 | LAB MANAGER ROOM,LAB QUALITY OFFICER | 80 | 100 | 1 PHASE,220-240V | 230 | KRUGER | RDC 450/6P
| REC-2 | 1 | RECEPTION | 175 | 100 | 1 PHASE,220-240V | 270 | KRUGER | CCD 8-8 180W 4P-1 1SK
| REC-3 | 1 | RECEPTION | 155 | 100 | 1 PHASE,220-240V | 230
Note: *Power consumption given are approximate, actual power consumption shall be consider as per equipment technical data sheet

## UH-01
Project Name - Medtrader Lab LLC
ELECTRIC UNIT HEATER
Description | Ref.Name | Area (Sq Ft) | Infiltration Loss | Exposed Area (Sq Ft) |  |  |  | U-Value - Ashrae 92.1-2010 |  |  | Delta T (°F) | Electric source |  |  |  | Remark
|  |  | Room Volume (Cu Ft) | Roof | Exterior | Window | Infiltration Factor | Roof | Exterior | Window |  | Heat Loss (Btu/Hr) | Heat Loss (KW) | Required Heating (KW) | Quantity (No.s)
Employee exchange-01 | GF-UH-01 | 269 | 3529.28 | 0 | 100 | 0 | 0.018 | 0.04 | 0.06 | 0.45 | 60 | 4171.6224 | 1.2219 | 1.3 | 1
Employee exchange-02 | GF-UH-02 | 269 | 3529.28 | 0 | 0 | 0 | 0.018 | 0.04 | 0.06 | 0.45 | 60 | 3811.6224 | 1.1165 | 1.3 | 1
Note
Given capacity is heating load. Electrical load shall be considered as per selection

## AIR CURTAIN
AIR CURTAIN
FLOOR SERVING | TAG | Qty | AREA | FLOW RATE L/s | STATIC PRESSURE (Pa) | POWER TYPE | ELECTRICAL POWER (W) | MAKE | MODEL
GROUND FLOOR | AIR CURTAIN-01 | 1 | RECEPTION DOOR - 2.1 METER | 1275 | 0 | 1 PHASE,220-240V | 580 | KRUGER | RDC 450/6P
| AIR CURTAIN-02 | 1 | RECEPTION- 1 METER | 540 | 0 | 1 PHASE,220-240V | 235 | KRUGER | CCD 8-8 180W 4P-1 1SK
Note: *Power consumption given are approximate, actual power consumption shall be consider as per equipment technical data sheet

## FRESH AIR FAN-R01
FRESH AIR FAN DETAILS
FLOOR SERVING | TAG | Qty | AREA / UNIT SERVED | FRESH AIR FLOW RATE L/s | STATIC PRESSURE (Pa) | FAN TYPE | POWER TYPE | ELECTRICAL POWER (W)
FIRST FLOOR | FF-FF-01 | 1 | 1F-IDU-1,2,3,9,10 | 91 | 70 | IN-LINE DIRECT DRIVEN CABINET FAN | 1-Phase,230V | 95
| FF-FF-02 | 1 | 1F-IDU-4,5,6,7,8 | 164 | 100 | IN-LINE DIRECT DRIVEN CABINET FAN | 1-Phase,230V | 178
Note: *Power consumption given are approximate, actual power consuption shall be consider as per equipment technical data sheet

## EXHAUST FAN-R01
EXHAUST AIR FAN DETAILS
FLOOR SERVING | TAG | Qty | AREA | FLOW RATE L/s | STATIC PRESSURE (Pa) | FAN TYPE | POWER TYPE | ELECTRICAL POWER (W) | MAKE | MODEL
GROUND FLOOR | GF-EF-01 | 1 | Extraction Room | 311 | 500 | ROOF TOP CENTRIFUGAL FAN | 1-Phase,230 V | 255 | KRUGER | RDC 450/6P
| GF-EF-02 | 1 | Received goods Check point | 88 | 70 | IN-LINE DIRECT DRIVEN CABINET FAN | 1-Phase, 230V | 70 | KRUGER | CCD 8-8 180W 4P-1 1SK
| GF-EF-03 | 1 |  | 88 | 70
| GF-EF-04 | 1 | Kitchen | 56 | 50 | CEILING MOUNTED TYPE | 1-Phase, 230V | 70
| GF-EF-05 | 1 | Employee exchange room | 160 | 50 | IN-LINE CENTRIFUGAL CIRCULAR FAN | 1-Phase, 230V | 120
| GF-EF-06 | 1 | Toilet-4,Toilet-5 | 50 | 50 | IN-LINE CENTRIFUGAL CIRCULAR FAN | 1-Phase, 230V | 70
| GF-EF-07 | 1 | 5 Nos of WC at patient reception | 125 | 50 | IN-LINE CENTRIFUGAL CIRCULAR FAN | 1-Phase, 230V | 120
| GF-EF-08 | 1 | Men, Women, Disabled Patients toilet & Sanitary room | 155 | 100 | IN-LINE DIRECT DRIVEN CABINET FAN | 1-Phase, 230V | 120
| GF-EF-09 | 1 | Bacteriology room /working area, Bacteriology preparation, Extraction room. Biosafety cabinet Exhaust | 306 | 100 | ROOF TOP CENTRIFUGAL FAN | 1-Phase,230 V | 255
| GF-EF-10 | 1 | Lab area . Biosafety cabinet Exhaust | 128 | 100 | ROOF TOP CENTRIFUGAL FAN | 1-Phase,230 V | 200
| GF-EF-11 | 1 | Biochemistry/microscope and cytology | 278 | 100 | ROOF TOP CENTRIFUGAL FAN | 1-Phase,230 V | 250
| GF-EF-12 | 1 | Autoclave & waste room | 150 | 100 | ROOF TOP CENTRIFUGAL FAN | 1-Phase,230 V | 120
FIRST FLOOR | 1F-EF-01 | 1 | Kitchen | 50 | 130 | CEILING MOUNTED TYPE | 1-Phase, 230V | 28
| 1F-EF-02 | 1 | Closet N1+WC+Closet N3 | 75 | 130 | INLINE CENTRIFUGAL CIRCULAR FAN | 1-Phase, 230V | 95
| 1F-EF-03 | 1 | Battery room | 36 | 50 | CEILING MOUNTED TYPE | 1-Phase, 230V | 25
Note: *Power consumption given are approximate, actual power consumption shall be consider as per equipment technical data sheet

## VAV & CANVAS
VAV DETAILS |  |  |  | CANVAS CONNECTION
SL NO | TAG | SIZE DIA (MM) | QTY |  | SIZE |  |  |  | LENGTH
1 | VAV-01 | 250 | 1 |  | MM | MM | MM | MM | MM | No.s | SQ.MT
2 | VAV-02 | 250 | 1 | 1 | 650 | 300 | 650 | 300 | 100 | 2 | 3.8
3 | VAV-03 | 250 | 1 | 2 | 1000 | 300 | 1000 | 300 | 100 | 3 | 7.8
4 | VAV-05 | 200 | 1 | 3 | 900 | 300 | 900 | 300 | 100 | 1 | 2.4
5 | VAV-04 | 250 | 1 | 4 | 850 | 300 | 850 | 300 | 100 | 1 | 2.3
6 | VAV-06 | 150 | 1 | 5 | 700 | 300 | 700 | 300 | 100 | 1 | 2
7 | VAV-07 | 200 | 1
8 | VAV-08 | 200 | 1 | TOTAL | [6 empty] | 18.3
21.96
TOTAL |  |  | 8

## CDP
DRAIN PIPE MEASUREMENT
S.NO | SIZE | LENGTH | TOTAL LENGTH
| MM | METER | METER
1 | 25 | 7.8 | 129.3
5.8
6.5
7.1
6.6
8
10.2
12.5
13
10
11.6
4.6
3
3.6
4
15
2 | 32 | 27.8 | 27.8
3 | 40 | 9.5 | 19
9.5

## Boq (hidden)
CLIENT : NMC
PROJECT : NMC SPECIALITY HOSPITAL
SCOPE ; MEP- HVAC, PLUMBING WORKS
LOCATION : 5TH & 6 TH FLOOR
BUDGETARY OFFER FOR MEP WORKS (ANNEXURE-2)
HVAC WORKS -5TH &6 TH FLOOR
S.No | Item Description | Unit | Qty | Unit Price | Total Price AED
1 | HVACworks-VRF system
Supply ,Installation,Testing & Commssioning of new factory Supplied Variable Refrigerant Flow System.
Supply of variable Refrigerant Flow airconditioning system complete with indoor & outdoor units with individual corded controller as per the design capaicties of the IDU and ODU.
1.1 | Supply,Installation ,Testing & Commssioning of Outdoor Units & Indoor units,Refrigerant Piping & ducting works | L.S | 1 | 330561 | 330561
1.4 | SITC of Drain Piping
| UPVC Schedule 40 drain piping for indoor units as per the design diameters of the pipes. The pipes shall be insulated with 6mm thick nitrile rubber | Rmtrs | 150 | 13.9207 | 2088.0987
2 | Supply,Installation,Testing & commssioning of Treated Fresh Air Handling Units - DX type-Floor mounted type with Prefilter 10 micron G4,Fine Filter,Mixing Box & accessories
a | Air flow 1794 L/s , Total Coil load 63 KW - FIFTH FLOOR
| (Double Skin Floor mounted FAHU with mixing Box) | No.s | 1 | 18125.9425 | 18125.9425
External Static Pressure 25 MM
b | Air flow 2090 L/s ,Total Coil load 77 KW - SIXTH FLOOR
| (Double Skin Floor mounted FAHU with mixing Box) | No.s | 1 | 18356.1132 | 18356.1132
External Static Pressure 25 MM
2.1 | Supply,Installation,Testing & commssioning of Air Handling Units - DX type-Floor mounted type with & prefilter 10 micron G4,Fine Filter,Mixing Box & accessories and condensing unit
A | Air flow 1347 L/s , Total Coil load 24.9 KW - 7 BED ICU
| External Static Pressure 20 MM | No.s | 1 | 17320.345 | 17320.345
with heater 2x2 Kw
B | Air flow 936 L/s , Total Coil load 15.8 KW - C SUCTION OT
| External Static Pressure75 MM | No.s | 1 | 13522.5285 | 13522.5285
with heater 1 Kw
C | Air flow 537 L/s , Total Coil load 9.1 KW - PREPARATION ROOM
| External Static Pressure 20 MM | No.s | 1 | 7423.005 | 7423.005
without heater
D | Air flow 739 L/s ,Total Coil load 8.5 KW- DELIVERY ROOM
| External Static Pressure 75 MM | No.s | 2 | 7423.005 | 14846.01
with heater 1.5 Kw
E | Air flow 385 L/s , Total Coil load 5.9 KW - STERILE STORE,CONSUMABLE STORE & SEMI STERILE
| External Static Pressure 20 MM | No.s | 1 | 4948.67 | 4948.67
with heater 1 Kw
2.2 | Supply,Installation,Testing & commssioning of Inline centrifugal fan as per design standards / shop drawings
a | Airflow 425 L/s - FIFTH FLOOR | No.s | 1 | 591.4037 | 591.4037
External Static Pressure 25 MM
b | Airflow 700 L/s- SIXTH FLOOR | No.s | 1 | 1278.36 | 1278.36
External Static Pressure 25 MM
2.3 | Supply of sheet metal machine made, prefabricated duct in accordance wit the approve shop drawings complete with all accessories like vanes,flanges,corners cleats,Gasket and as required specifications. For FAD works with supporting arrangements
| 24 Guage | Sq.mtrs | 500 | 67.2763 | 33638.1344
| 22 Gauge | Sq.mtrs | RO | 83.693
2.4 | Supply of sheet metal machine made, prefabricated duct in accordance wit the approve shop drawings complete with all accessories like vanes,flanges,corners cleats,Gasket and as required specifications. For EAD works with supporting arrangements
| 24 Guage | Sq.mtrs | 250 | 67.2763 | 16819.0672
| 22 Gauge | Sq.mtrs | RO | 83.693
2.5 | Refrigerant Piping
| Supply and installation ,Testing Commissioning of Refrigerant Copper piping insulated with Nitrile Rubber Tubular Insulation | Rmtrs | 440 | 114 | 50160
note : condensing side copper piping considered 6 rmtrs maximum exceeding will be additional chargable
3 | THERMAL/ ACCOUSTIC INSULATION
3.1 | Supply and fixing of external insulation on supply & return air ducts as per specification. Material of insulation shall be closed cell crosslinked polyethelene/Nitrile rubber as per thickness given below:
a | 13 mm thick Thermal insulation | Sq.mtrs | 600 | 36 | 21600
b | 10 mm thick accoustic lining | Sq.mtrs | 20 | 72 | 1440
3.2 | Supply ,Installation of Volume Control damper as per the designed specifications | Sq.mtrs | 10 | 440 | 4400
3.4 | Supply ,Installation ,Testing & Commissioning of DDC Panel with all necessary cabling works as per design standards | Unit | 1 | 26998.2 | 26998.2
3.5 | Supply ,Installation of Grills & Diffusers | Sq.mtrs | 10 | 774.4572 | 7744.572
3.6 | Supply ,Installation of Sand Trap / Extract Air Louvers | Sq.mtrs | 1 | 309.7829 | 309.7829
3.7 | Supply & installation of Aluminium cladding ( 0.6 mm thk AL sheet) for Exposed duct area | Sq.mtrs | 11 | 49.8704 | 548.5738
3.8 | Allow for submission of Submittals & Drawing samples | L.S | 1 | 1000 | 1000
3.9 | Allow for Painting & identification Equipments & units | L.S | 1 | 500 | 500
| TOTAL PRICE FOR 5F TO 6TH FLOOR HVAC WORKS |  |  |  | 594219.8068
PLUMBING WORKS -5TH &6 TH FLOOR
S.No | Item Description | Unit | Qty | Unit Price | Total Price AED
A. | SANITARY FIXTURES & FITTINGS
1.1 | Supply,Installation ,Testing & Commissioning of European Water Closet with seat cover, & Health Faucet, Flush tank , angle valve, track bolt and accessories | No.s | 30 | 1074.0276 | 32220.8278
1.2 | Supply,Installation ,Testing & Commissioning of Wash basin with ,CI / MS brackets angle cock, trap and accessories
| FLAT BACK WITH BASIN MIXER | No.s | 28 | 394.1188 | 11035.3261
| FLAT BACK WITH PILLAR COCK | No.s | 33 | 444.7304 | 14676.1017
1.3 | Supply,Installation ,Testing & Commissioning of Water heater with bracket,angle valve,flexible hose | No | RO | 492.8364
1.4 | Supply,Installation & Testing of Sink with mixer ,braided hose,angle valve, tap | No | RO | 492.8364
1.5 | Supply,Installation & Testing of Bibcock | No | 30 | 72.2566 | 2167.6977
1.55 | Supply,Installation & Testing of Shower set with accessories Over head Shower,Spout,diverter,shower tray etc. | No | 25 | 539.7732 | 13494.33
B. | Drainage/Domestic water supply Piping works
1.6 | Supply,Installation & Testing of UPVC SWR pipes for drainage /waste water line works
1.61 | 110 mm dia | Rmtrs | 450 | 30.7594 | 13841.7275
1.62 | 75 mm dia | Rmtrs | 356 | 30.7594 | 10950.3444
1.63 | 50 mm dia | Rmtrs | 250 | 21.0138 | 5253.4609
2.2 | Supply,Installation & Testing of PPR(PN 20 )pipes for domestic/ cold /hot water line works
1.63 | 50 mm dia | Rmtrs | 100 | 108.9165 | 10891.65
2.25 | 32 mm dia | Rmtrs | 100 | 41.0205 | 4102.05
2.5 | 25 mm dia | Rmtrs | 275 | 25.461 | 7001.775
2.75 | 20 mm dia | Rmtrs | 300 | 14.145 | 4243.5
2.78 | 15 mm dia | Rmtrs | 100 | 11 | 1100
3 | Supply,Installation & Testing of 110 X 75 mm multi floor trap with SS Gratings | No.s | 25 | 337.3582 | 8433.9562
3.1 | Supply,Installation & Testing of Brass Ball Valve for Domestic & hotwater line
3.15 | 15 mm dia | No.s | 50 | 108 | 5400
3.2 | 20 mm dia | No.s | 40 | 121.8896 | 4875.5845
3.3 | 25 mm dia | No.s | 30 | 138.0454 | 4141.3619
3.4 | 32 mm dia | No.s | 30 | 138.0454 | 4141.3619
3.5 | 50 mm dia | No.s | 20 | 160 | 3200
4 | Supplying, Installing & Testing at site in position micro cellular closed cell Nitrile rubber elastomeric insulation (UL-94 Approved) tubes/ sheets(9mm thick) for the hot water supply pipes with protective glass fabric & co-extruded polymeric covering for UV & mechanical protection.
4.1 | 15 mm | Rmtrs | 120 | 9 | 1080
4.15 | 20 mm | Rmtrs | 100 | 10.9007 | 1090.0724
4.2 | 25 mm | Rmtrs | 20 | 12.2633 | 245.2663
4.3 | 32 mm | Rmtrs | 30 | 14 | 420
4.1 | 40 mm | Rmtrs | 50 | 16 | 800
4.2 | 50 mm | Rmtrs | 50 | 18 | 900
4.4 | Allow for submission of Submittals & Drawing samples | L.S | 1 | 1000 | 1000
4.5 | Allow for Painting & identification Equipments & units | L.S | 1 | 500 | 500
| TOTAL PRICE FOR 5F TO 6TH FLOOR PLUMBING WORKS |  |  |  | 167206.3945