## заявка
N | Product Description | Tech Specifications | Unit | QTY
1 | Clamping device FHG51-AA1+Z1 | Item's material - stainless steel 316L | piece | 1
2 | Electromagnetic flowmeter | Power supply 24 V DC, 4-wire connection, analog active output 4-20 mA, error - no more than 0,5% of scale, Hart protocol support, remote 4-line display, for non-hazardous area, process connection - Flange Dn125mm (EN1092-1), max.operational pressure 16 bar, body material - stainless steel, operating temperature -25...+50C, IP67 or higher, measuring medium - water, liner's material should correspond to measuring medium, factory calibration for a range 0 - 100 m3/hour, 2 cable glands M20*1,5mm. | piece | 1
3 | Ultrasonic Level Transmitter | Power supply 24 V DC, 2-wire connection, analog output 4-20 mA, error - no more than 0,2% of scale, Hart protocol support, 4-line graphic display, for non-hazardous area, process connection - Flange Dn80mm (EN1092-1), maximum measured distance - 10 meters, body material - aluminium, operating temperature -25...+50C, IP67 or higher, measuring medium - pulp, medium density - 1,1 - 2 kg/m3, 1 cable gland M20*1,5mm. | piece | 1
4 | Ultrasonic Level Transmitter | Power supply 24 V DC, 2-wire connection, analog output 4-20 mA, error - no more than 0,2% of scale, Hart protocol support, 4-line graphic display, for non-hazardous area, process connection - thread G2", maximum measured distance - 8 meters, body material - aluminium, operating temperature -25...+50C, IP67 or higher, measuring medium - pulp, medium density - 1,1 - 2 kg/m3, 1 cable gland M20*1,5mm. | piece | 1
5 | Vibronic Point level detection | Power supply 24 V DC, 2-wire connection, relay output DPDT, material of a sensor - stainless steel, material of a body - aluminium/plastic, lenght of sensor - 1,2 meter, for non-hazardous area, process connection - thread G1", measuring medium - pulp, medium density - 1,1 - 1,8 kg/m3, 1 cable gland M20*1,5mm. | piece | 2
6 | Vibronic Point level detection | Power supply 24 V DC, 2-wire connection, relay output DPDT, material of a sensor - stainless steel, material of a body - aluminium/plastic, lenght of sensor - 0,4 meter, for non-hazardous area, process connection - thread G1", measuring medium - pulp, medium density - 1,1 - 1,8 kg/m3, 1 cable gland M20*1,5mm. | piece | 2
7 | Profinet - Ethernet IP Gateway | Prosoft PLX32-EIP-PND | piece | 1
8 | Ultrasonic Level Transmitter | Power supply 24 V DC, 2-wire connection, analog output 4-20 mA, error - no more than 0,2% of scale, Hart protocol support, 4-line graphic display, for non-hazardous area, process connection - thread G2", maximum measured distance - 6 meters, body material - aluminium, operating temperature -25...+50C, IP67 or higher, measuring medium - water, 1 cable gland M20*1,5mm. | piece | 1
9 | Pressure Transmitter | Power supply 24 V DC, 2-wire connection, analog output 4-20 mA, error - no more than 0,1% of scale, Hart protocol support, graphic display, for non-hazardous area, process connection - thread G1/2", measured range - 0 - 20bar, body material - aluminium, operating temperature -25...+50C, IP67 or higher, measuring medium - water, 1 cable gland M20*1,5mm. | piece | 1

## Sheet1 (hidden)
საქონელი | RMG Copper
მომსახურება | RMG Gold
Auramine